## Sheet1
ZONE | DIVISION | VOLTAGE | SEVERITY | STATION1 | FROM SWITCH | STATION2 | TO SWITCH | CABLE_SIZE | DESCRIPTION_CABLE_TYPE | EVENT_TIME | EVENT_TIME_24 | EVENT_TIME_MONTH | SECTION_FROM_DSS | PENDING_DAYS | TARGET_RECTIFICATION_DATE | LOAD_BEFORE_TRIPPING | LOAD_ON_SECTION | EXTRA_LOAD_ON_SECTION | NO_OF_OPERATIONS | DESCRIPTION_CABLE_ROUTE_INSP | FAULT_REPETATION_DETAILS | RADIAL_SUBSTATIONS | TITLE | OTHERS_REMARKS | CURRENT_FAULT_STATUS | DESCRIPTION_CABLE_FAULT_NATURE | CABLE FAULT NATURE | ADD_VALUE | DESC_VALUE | DESCRIPTION_RED_FLAG | SEASON | NORMAL_FEEDER_PEAK_LOAD | NORMAL_FEEDER_PEAK_LOAD_TIME | NORMAL_AVG_PEAK_LOAD | LOAD_FACTOR_OF_FEEDER | MAXTEMP | MAX_DEMAND_MW | RAIN | HEAT_INDEX | CREATION_DATE | RECEIVING_STATION | CREATION_TIME | DESCRIPTION
3000 |  | 11 KV | CRITICAL | BHULLAR VILLA | 39949 | AKSA BEACH | 7869 | 240+300 | PILC+XLPE | 2024-11-11 15:27:00.000000 UTC | 2024-11-11 15:27 | 11 | 4 | 56 | 2024-11-14 23:53:28.000000 UTC | 120 | 105 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 3 | Y phase faulty at a distance of 122 meters from Aksa Beach Substation Switch Number 7869 . Fault pinpointed NEAR ST.LIGHT POLE NO. PCW004064. Shown to REDDY. Total length 1222 meter. |  |  | 1 | Running Cable Fault |  | Fault Details | LOAD CURTAILMENT FOR (N-2) SYSTEM | WINTER | 170 | 140 | 140 | 0.82 | 33.2 | 1694 | 0 | 33.76 |  | ERANGLE REC-STN | 2024-11-11 15:44:29.000000 UTC | Section
7000 |  | 11 KV | MODERATE | ANGOLIMALA | 30632 | NEHRU NGR 3 | 43054 | 225+240+300 | PILC+XLPE | 2024-11-11 16:04:00.000000 UTC | 2024-11-11 16:04 | 11 | 6 | 56 | 2024-11-15 23:17:15.000000 UTC | 60 | 30 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 2 | 4 | B Phase Faulty at 160 Meters from ANGOLIMALA Fault Pinpointed at ON S G BARVE MARG NEAR NEHARU NGR NO 3 Total length : 210 Meters. |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 80 | 00:14:00 | 65 | 0.81 | 33.26 | 1694 | 0 | 33.76 | 2024-11-14 20:43:23.000000 UTC | CHUNABHATTI REC-STN | 2024-11-11 21:03:49.000000 UTC | Section
7000 |  | 11 KV | MODERATE | SAMATA VIDYALAYA | 31943 | REHAB HSG 2 | 25766 | 300 | XLPE | 2024-11-11 16:00:00.000000 UTC | 2024-11-11 16:00 | 11 | 3 | 56 | 2024-11-13 23:14:38.000000 UTC | 56 | 18 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 2 | 1 | Y Phase Faulty at 381 Meters from REHAB HSG 2 Fault Pinpointed at Fault pinpointed IN MACCHIMARKET NEARE CROSSIMG CULVERT LALLUBHAI COMPOUND ON ZAKIR HUSEN RD. Shown to SHANKAR. Total length 490 meter. |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 73 | 01:02:00 | 60 | 0.82 | 33.26 | 1694 | 0 | 33.76 | 2024-11-13 19:36:49.000000 UTC | SHIVAJI NAGAR REC-STN | 2024-11-11 20:55:44.000000 UTC | Section
3000 |  | 11 KV | MODERATE | KANDIVLI INDUSTRIES NO.6 | 4269 | KISHCO NO.1 | 4682 | 300 | XLPE | 2024-11-11 11:29:00.000000 UTC | 2024-11-11 11:29 | 11 | 2 | 56 | 2024-11-14 22:48:37.000000 UTC | 84 | 64 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 2 | B phase faulty at a distance of 186 meters from Kishco No.1 Substation Switch Number 4682 . Fault pinpointed KANDIVALI INDUSTRIAL INTERNAL ROAD AT T JUNCTION NEAR TATA PILLAR . Shown to KRISHNA MURTHY. Total length 203 meter. |  | SYSTEM NORMALIZE | 4 | Fault Bypassed |  | Fault Details |  | WINTER | 90 | 12:14:00 | 65 | 0.72 | 33.26 | 1964 | 0 | 33.76 | 2024-11-15 18:40:58.000000 UTC | K.I.E. REC-STN | 2024-11-11 15:51:02.000000 UTC | Section
4000 |  | 11 KV | CRITICAL | BHARUCHA ROAD | 7430 | KRISHNA TOWER | 11675 | 120 | PILC | 2024-11-07 02:59:00.000000 UTC | 2024-11-07 02:59 | 11 | 4 | 60 | 2024-11-09 07:27:22.000000 UTC | 35 | 10 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 1 | 5 | R Phase Faulty at 54 Meters from KRISHNA TOWER Fault Pinpointed at IN FRONT OF KALA DIAGNOSTIC CENTRE NEAR POLE RFV001043 . SHOWN TO SANTOSH. Total length : 214 Meters. |  |  | 1 | Running Cable Fault |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | WINTER | 58 | 18:04:00 | 43 | 0.74 | 35.61 | 1727 | 0 | 39.64 |  | DAHISAR REC-STN | 2024-11-07 03:21:30.000000 UTC | Section
3000 |  | 11 KV | MODERATE | KASTURBA ROAD | 6163 | NIVATIA ROAD NO.3 | 35343 | 120+150+300 | PILC+XLPE | 2024-11-07 11:28:00.000000 UTC | 2024-11-07 11:28 | 11 | 6 | 60 | 2024-11-11 12:36:05.000000 UTC | 98 | 45 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 3 | 1 |  |  |  | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 140 | 15:41:00 | 106 | 0.76 | 35.61 | 1727 | 0 | 39.64 |  | CHINCHAVLI REC-STN | 2024-11-07 12:32:38.000000 UTC | Section
1000 |  | 11 KV | MODERATE | SANTACRUZ REC-STN | 30482 | GOLIBAR PIPE LINE | 11642 | 240+300 | PILC+XLPE | 2024-09-26 21:42:59.000000 UTC | 2024-09-26 21:43 | 9 | 1 | 102 | 2024-09-28 08:02:29.000000 UTC | 32 | 32 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 12 | 2 | R phase faulty at a distance of 1200 meters from Golibar Pipe Line Sub Station Switch Number 11642 . Fault pinpointed ON WESTERN HIGHWAY SERVICE ROAD NEAR MCGM CHOUKY OPPO. VAKOLA METRO STATION. Shown to SHARAD. Total length 1900 meter. |  |  | 19 | Transition Joint Faulty |  | Fault Details |  | MONSOON | 38 | 08:22:00 | 30 | 0.79 | 27.77 | 1757 | 27.5 | 34.02 |  | SANTACRUZ REC-STN | 2024-09-26 21:45:34.000000 UTC | Section
2000 |  | 11 KV | MODERATE | VERSOVA RECEIVING STATION | 26206 | GODREJ WALROF | 28057 | 300+400 | XLPE | 2024-09-26 01:50:00.000000 UTC | 2024-09-26 01:50 | 9 | 1 | 102 | 2024-10-10 23:00:44.000000 UTC | 45 | 45 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 3 | 3 | R Phase Faulty at 65 Meters from GODREJ WALROF Fault Pinpointed at NEAR TO LT 6 WAY PILLAR 19060823, IN FRONT OF ASHISH BUILDING, ON MILLAT NAGAR ROAD Total length : 2150 Meters. |  |  | 1 | Running Cable Fault |  | Fault Details |  | MONSOON | 75 | 15:06:00 | 54 | 0.72 | 24.74 | 1816 | 10 | 25.78 |  | VERSOVA RECEIVING STATION | 2024-09-26 04:28:34.000000 UTC | Section
4000 |  | 11 KV | MODERATE | DAHISAR PARIJAT | 15229 | RAWALPADA | 7729 | 240+300 | PILC+XLPE | 2024-11-05 11:09:00.000000 UTC | 2024-11-05 11:09 | 11 | 3 | 62 | 2024-11-09 01:30:41.000000 UTC | 82 | 65 | 0 | 0 | EXCAVATION ALONG THE ROUTE |  | 1 |  |  | SYSTEM NORMALIZE | 22 | Cable Damaged |  | Fault Details |  | MONSOON | 89 | 09:23:00 | 80 | 0.9 | 41.97 | 1762 | 0 | 36.24 | 2024-11-06 00:29:46.000000 UTC | DAHISAR REC-STN | 2024-11-05 11:39:29.000000 UTC | Section
1000 |  | 11 KV |  | MADHAVA | 26119 |  |  |  |  | 2024-11-05 15:35:15.000000 UTC | 2024-11-05 15:35 | 11 |  | 62 | [10 empty] | SYSTEM NORMALIZE | 5 | Termination Faulty |  | Fault Details | [10 empty] | 2024-11-06 16:45:58.000000 UTC | KALANAGAR REC-STN | 2024-11-05 16:13:00.000000 UTC | Breaker/Switch
4000 |  | 11 KV | MODERATE | ROKADIA LANE | 7142 | MOHANDAS PARK | 12416 | 70+120 | PILC | 2024-11-05 09:51:00.000000 UTC | 2024-11-05 09:51 | 11 | 2 | 62 | 2024-11-09 01:30:41.000000 UTC | 61 | 0 | 0 | 0 | EXCAVATION ALONG THE ROUTE |  | 0 |  |  |  | 22 | Cable Damaged |  | Fault Details |  | MONSOON | 94 | 18:23:00 | 67 | 0.71 | 41.97 | 1762 | 0 | 36.24 |  | DEVIDAS LANE REC-STN | 2024-11-05 10:54:21.000000 UTC | Section
7000 |  | 11 KV | MODERATE | CHEMBUR EASTERN COURT | 37095 | VIJAY CINEMA | 14739 | 240+300 | PILC+XLPE | 2024-11-04 09:25:00.000000 UTC | 2024-11-04 09:25 | 11 | 7 | 63 | 2024-11-08 07:41:30.000000 UTC | 106 | 20 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 3 | 3 |  | CABLE BURNT AT BHOJ BHAVAN BLDG | SYSTEM NORMALIZE | 31 | Cable Burnt |  | Fault Details |  | WINTER | 120 | 91 | 91 | 0.76 | 35.08 | 1746 | 0 | 28.11 | 2024-11-06 19:15:40.000000 UTC | SIDHARTH NAGAR RECEIVING STATION | 2024-11-04 11:27:00.000000 UTC | Section
2000 |  | 11 KV | MODERATE | YAMUNA NAGAR NO.1 | 7861 | ST.LAURENCE SCHOOL | 31608 | 120+150 | PILC+XLPE | 2024-11-05 11:09:10.000000 UTC | 2024-11-05 11:09 | 11 | 6 | 62 | 2024-11-10 07:24:15.000000 UTC | 45 | 0 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 3 | 4 |  |  |  | 22 | Cable Damaged |  | Fault Details |  | WINTER | 71 | 21:00:00 | 50 | 0.7 | 36.24 | 1762 | 0 | 41.97 |  | SWAMI SAMARTH NAGAR RECEIVING STATION | 2024-11-05 11:31:06.000000 UTC | Section
2000 |  | 11 KV | MODERATE | WORLD BANK | 15630 | RESHAM | 9370 | 300 | XLPE | 2024-11-05 12:23:00.000000 UTC | 2024-11-05 12:23 | 11 | 6 | 62 | 2024-11-10 07:29:15.000000 UTC | 87 | 0 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 5 | 0 |  |  |  | 22 | Cable Damaged |  | Fault Details |  | WINTER | 140 | 22:30:00 | 110 | 0.79 | 36.24 | 1762 | 0 | 41.97 |  | VERSOVA RECEIVING STATION | 2024-11-05 15:10:24.000000 UTC | Section
7000 |  | 22 KV | CRITICAL | TATA''S CHEMBUR REC-STN | T22CHMBOG03 | CHEMBUR REC-STN | 1151 | 300 | PILC | 2024-11-04 16:28:00.000000 UTC | 2024-11-04 16:28 | 11 |  | 63 | 2024-11-11 07:43:34.000000 UTC | 120 |  |  |  | NO EXCAVATION ALONG THE ROUTE | 20 |  | R Phase Faulty at 2375 Meters from CHEMBUR R/S Fault Pinpointed at Fault pinpointed RCF COLONY NEAR ASHOK BHUDDHA VIHAR. Total length : 3286 Meters. |  | SYSTEM NORMALIZE | 23 | Straight Joint Faulty |  | Fault Details | 22kV Cable fault | [9 empty] | 2024-11-11 21:47:58.000000 UTC | TATA''S CHEMBUR REC-STN | 2024-11-04 16:36:31.000000 UTC | Incommer Line
2000 | ANDHERI | 22 KV | CRITICAL | TATA''S SAKI REC-STN | T22SAKOG09 | M.I.D.C. REC-STN | 33063 | 300+400 |  | 2024-11-02 01:40:00.000000 UTC | 2024-11-02 01:40 | 11 |  | 65 | 2024-11-05 07:45:55.000000 UTC | 32 |  |  |  | NO EXCAVATION ALONG THE ROUTE | 20 |  | No-Fault after testing. All three phases stood ok at KV for Mins. Total Length meters. Remarks |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details | 22kV Cable fault | [9 empty] | 2024-11-10 00:20:43.000000 UTC | TATA''S SAKI REC-STN | 2024-11-02 01:52:38.000000 UTC | Incommer Line
1000 |  | 11 KV | MODERATE | KHAR EXCHANGE | 1013 | SIXTEENTH ROAD (16TH ROAD) | 5952 | 120 | PILC | 2024-11-01 22:41:00.000000 UTC | 2024-11-01 22:41 | 11 | 6 | 66 | 2024-11-15 07:49:42.000000 UTC | 102 | 0 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 6 | 0 | Y phase faulty at a distance of 121 meters from Khar Exchange Sub Station Switch Number 1013 . Fault pinpointed ON KHAR PALI ROAD, OPP PUNJAB SIND DAIRY NEAR STREET LIGHT POLE HAG053 011. Shown to GOPI. Total length 447 meter. |  |  | 4 | Fault Bypassed |  | Fault Details |  | WINTER | 169 | 102 | 102 | 0.6 | 34.28 | 1710 | 0 | 48.33 |  | 24TH ROAD REC-STN | 2024-11-02 00:54:39.000000 UTC | Section
4000 |  | 11 KV | MODERATE | CABLE STAFF | 9235 | KULUP WADI | 17427 | 300+400 | XLPE | 2024-11-03 14:55:00.000000 UTC | 2024-11-03 14:55 | 11 | 5 | 64 | 2024-11-07 23:48:46.000000 UTC | 31 | 0 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 2 |  |  |  | 22 | Cable Damaged |  | Fault Details |  | WINTER | 42 | 20:30:00 | 33 | 0.79 | 36.3 | 1597 | 0 | 43.63 |  | BORIVALI REC-STN | 2024-11-03 16:03:44.000000 UTC | Section
1000 |  | 11 KV | CRITICAL | SHREE GANESH | 9850 | SEVENTEEN ROAD | 6368 | 120+150 | PILC | 2024-09-18 23:16:00.000000 UTC | 2024-09-18 23:16 | 9 | 15 | 110 | 2024-09-20 07:54:04.000000 UTC | 123 | 10 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 6 | 9 | RYB Phase Faulty at 40 Meters from SEVENTEEN ROAD Fault Pinpointed at NEAR EXOTIQUE BLDG OPPOSITE LT MP 11081027. |  |  | 19 | Transition Joint Faulty |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | SUMMER | 134 | 19:58:00 | 114 | 0.85 | 32.81 | 1742 | 0 | 42.37 |  | BANDRA REC-STN | 2024-09-19 00:09:05.000000 UTC | Section
5000 |  | 11 KV | CRITICAL | SHREE PARK BUILDING | 30558 | INDRAJEET | 18881 | 300 | XLPE | 2024-09-18 11:15:00.000000 UTC | 2024-09-18 11:15 | 9 | 7 | 110 | 2024-09-21 21:29:24.000000 UTC | 126 | 20 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 1 | 5 | Fault Pinpointed at B phase faulty at a distance of 360 meters from Indrajeet Sub Station Switch Number 18881 . Fault pinpointed ON MIRA BHAYANDER ROAD OPPO HAPPY CAR WORLD SHOWROOM & OPPO SMART HOTEL EQUIPMENT. Shown to KISHTYA. Total length 1200 meter. |  |  | 4 | Fault Bypassed |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | MONSOON | 140 | 10:44:00 | 107 | 0.76 | 31.79 | 1787 | 0 | 44.37 |  | VINAMRA REC-STN | 2024-09-18 12:08:20.000000 UTC | Section
2000 |  | 11 KV |  | CHARAT SINGH COLONY NO.2 | 15066 |  |  |  |  | 2024-09-17 12:15:00.000000 UTC | 2024-09-17 12:15 | 9 |  | 111 | [10 empty] | SYSTEM NORMALIZE | 37 | DT ID Box Flashover |  | Fault Details | [10 empty] | 2024-09-18 15:12:51.000000 UTC | CHARAT SINGH COLONY NO.2 | 2024-09-18 15:11:49.000000 UTC | DT/LTB
1000 |  | 11 KV | CRITICAL | SUMIT ARTISTA | 39925 | MHADA HIG | 41234 | 300 | XLPE | 2024-11-21 17:20:00.000000 UTC | 2024-11-21 17:20 | 11 | 9 | 46 | 2024-11-22 23:05:41.000000 UTC | 74 | 30 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 3 | 5 | Y Phase Faulty at 150 Meters from sumit arrista Fault Pinpointed at Fault pinpointed ON CST RD , NEAR HARE KRISHNA HOSTEL, OPPOSITE AISHWARYA TOWER GATE. Total length : 240 Meters. |  |  | 1 | Running Cable Fault |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | WINTER | 119 | 00:27:00 | 91 | 0.76 | 32.92 | 1609 | 0 | 34.59 |  | KALINA REC-STN | 2024-11-21 17:41:18.000000 UTC | Section
1000 |  | 11 KV | CRITICAL | K.L.S. MEMORIAL HOSPITAL | 35964 | MATOSHREE KUNJ | 32974 | 150+300 | XLPE | 2024-11-21 16:01:00.000000 UTC | 2024-11-21 16:01 | 11 | 2 | 46 | 2024-11-21 17:17:33.000000 UTC | 24 | 14 | 0 | 0 | EXCAVATION ALONG THE ROUTE |  | 6 |  |  |  | 22 | Cable Damaged |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | WINTER | 32 | 22:23:00 | 21 | 0.66 | 32.92 | 1609 | 0 | 34.59 |  | JUHU REC-STN | 2024-11-21 16:42:50.000000 UTC | Section
3000 | MALAD | 33 KV | CRITICAL | 220kV GOREGAON REC-STN | 220GOR32 | MAHANANDA REC-STN | 33160 | 400 | XLPE | 2024-11-21 17:26:00.000000 UTC | 2024-11-21 17:26 | 11 |  | 46 | 2024-11-23 23:04:17.000000 UTC | 32 |  |  |  | NO EXCAVATION ALONG THE ROUTE | 1 |  | B phase faulty at a distance of 1100 meters from Mahananda R/S Switch Number 33160 . Fault pinpointed BELOW GOREGAON METRO STATION ON W-E-HIGHWAY ,INFRONT OF GATE ENTRY NO.710. Shown to MUTTU. Total length 3200 meter. |  |  | 21 | System Re-Arrangement Done |  | Fault Details | 33kV Cable fault | [10 empty] | 220kV GOREGAON REC-STN | 2024-11-21 18:30:58.000000 UTC | Incommer Line
4000 |  | 11 KV | MODERATE | GURUKUL TOWER | 15961 | RANGNATH KESKAR ROAD | 29877 | 120+150+300 | PILC+XLPE | 2024-11-21 14:54:00.000000 UTC | 2024-11-21 14:54 | 11 | 2 | 46 | 2024-11-23 18:05:52.000000 UTC | 15 | 15 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 3 | 3 |  |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 74 | 60 | 60 | 0.81 | 32.92 | 1609 | 0 | 34.59 | 2024-11-23 19:20:32.000000 UTC | RANGNATH KESKAR ROAD | 2024-11-21 17:56:39.000000 UTC | Section
1000 |  | 11 KV | CRITICAL | LOTUS MID TOWN | 34405 | KALINA SOUTH NO.1 | 26126 | 300 | XLPE | 2024-11-21 16:34:30.000000 UTC | 2024-11-21 16:35 | 11 | 4 | 46 | 2024-11-25 17:17:58.000000 UTC | 143 | 40 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 1 | Y phase faulty at a distance of 71 meters from Kalina South No.1 Sub Station Switch Number 26126 . Fault pinpointed WINDSOOR ROAD, OPPOSITE WIDENSON FINANCIAL BLDG. Shown to SHARAD. Total length 160 meter. |  |  | 1 | Running Cable Fault |  | Fault Details | PRIME AREA | WINTER | 164 | 11:30:00 | 134 | 0.82 | 32.92 | 1609 | 0 | 34.59 |  | GODREJ BKC REC-STN | 2024-11-21 16:53:07.000000 UTC | Section
1000 |  | 11 KV | MODERATE | BANDRA REC-STN | 41910 | HI-CONS RESIDENCY | 31116 | 240+300 | PILC+XLPE | 2024-10-06 03:32:00.000000 UTC | 2024-10-06 03:32 | 10 | 1 | 92 | 2024-10-09 07:33:48.000000 UTC | 70 | 70 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 8 | 1 | Y Phase Faulty at 175 Meters from HI-CONS RESIDENCY Fault Pinpointed at Fault pinpointed OPPOSITE TO BORA BORA RESTAURANT |  |  | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 112 | 80 | 80 | 0.71 | 34.85 | 1671 | 0 | 36.27 |  | BANDRA REC-STN | 2024-10-06 04:12:14.000000 UTC | Section
7000 |  | 11 KV | MODERATE | AERB OFFICE COMPLEX | 12965 | UDAYGIRI | 32295 | 240+300 | PILC+XLPE | 2024-10-06 09:57:00.000000 UTC | 2024-10-06 09:57 | 10 | 3 | 92 | 2024-10-10 07:18:09.000000 UTC | 12 | 12 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 4 | 0 | Y Phase Faulty at 115 Meters from UDAYGIRI Fault Pinpointed at VN PURAV MARG , NEAR BARC COMPOUND AND NALA Total length : 607 Meters. |  | SYSTEM NORMALIZE | 19 | Transition Joint Faulty |  | Fault Details |  | MONSOON | 26 | 09:20:00 | 14 | 0.54 | 34.85 | 1671 | 0 | 52.72 | 2024-10-09 18:58:47.000000 UTC | CHEMBUR REC-STN | 2024-10-06 12:29:23.000000 UTC | Section
4000 |  | 11 KV |  | AIR BORIVALI | 13248 |  |  |  |  | 2024-10-06 17:45:00.000000 UTC | 2024-10-06 17:45 | 10 |  | 92 | [10 empty] | SYSTEM NORMALIZE | 57 | HT Consumer Network Problem |  | Fault Details | [10 empty] | 2024-10-07 22:15:01.000000 UTC | AIR BORIVALI | 2024-10-06 19:13:37.000000 UTC | HT Consumer
1000 |  | 11 KV | MODERATE | BHARAT NAGAR NO.3 | 9664 | PATHAR NAGAR NO 2 | 38978 | 240+300 | PILC+XLPE | 2024-10-08 17:18:00.000000 UTC | 2024-10-08 17:18 | 10 | 5 | 90 | 2024-10-11 19:44:28.000000 UTC | 145 | 0 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 5 | 2 |  |  |  | 1 | Running Cable Fault |  | Fault Details |  | MONSOON | 155 | 10:59:00 | 90 | 0.58 | 35.08 | 1998 | 0 | 52.36 |  | MMRDA REC-STN | 2024-10-08 17:59:48.000000 UTC | Section
3000 |  | 11 KV |  | SUNDER NAGAR NO.3 | 42559 |  |  |  |  | 2024-10-08 12:35:00.000000 UTC | 2024-10-08 12:35 | 10 |  | 90 | [10 empty] | SYSTEM NORMALIZE | 34 | DT Abnormality |  | Fault Details | [10 empty] | 2024-10-09 02:48:22.000000 UTC | SUNDER NAGAR NO.3 | 2024-10-09 02:46:50.000000 UTC | DT/LTB
4000 | BORIWALI | 33 KV | CRITICAL | 220kV GORAI REC-STN | 220GOI18 | RNA ROYAL PARK REC-STN | 33172 | 400 |  | 2024-10-08 05:19:50.000000 UTC | 2024-10-08 05:20 | 10 |  | 90 | 2024-10-11 06:23:37.000000 UTC | 360 |  |  |  | NO EXCAVATION ALONG THE ROUTE |  |  |  |  | SYSTEM NORMALIZE | 8 | Switchgear Support Insulator Faulty |  | Fault Details | 33kV Cable fault | [9 empty] | 2024-10-21 23:24:34.000000 UTC | 220kV GORAI REC-STN | 2024-10-12 07:31:01.000000 UTC | Breaker/Switch
1000 |  | 11 KV | CRITICAL | THIRD ROAD (3RD) | 30975 | FORTUNE PARADISE | 36876 | 185+240+300 | PILC+XLPE | 2024-11-29 16:19:00.000000 UTC | 2024-11-29 16:19 | 11 | 8 | 38 | 2024-11-30 23:01:50.000000 UTC | 125 | 35 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 3 | 6 |  |  |  | 22 | Cable Damaged |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | WINTER | 129 | 16:20:00 | 62 | 0.48 | 30.95 | 1481 | 0 | 29.51 |  | 24TH ROAD REC-STN | 2024-11-29 16:54:39.000000 UTC | Section
1000 |  | 11 KV | CRITICAL | DHIRAJ RESIDENCY NO.2 | 19693 | RAMA''S PLAZA | 34871 | 300 | XLPE | 2024-11-29 14:34:35.000000 UTC | 2024-11-29 14:35 | 11 | 5 | 38 | 2024-11-30 23:58:18.000000 UTC | 126 | 60 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 2 | R phase faulty at a distance of 180 meters from Rama'S Plaza Sub Station Switch Number 34871 . Fault pinpointed LABISA SHOP OPPOSITE RELIANCE DIGITAL MALL.. Shown to SHARAD. Total length 675 meter. |  |  | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 133 | 15:30:00 | 87 | 0.65 | 30.95 | 1481 | 0 | 29.51 |  | VERSOVA RECEIVING STATION | 2024-11-29 15:26:36.000000 UTC | Section
2000 |  | 11 KV | MODERATE | LAXMI INDUSTRIAL ESTATE NO.1 | 19605 | MOHAN BAKERY | 19780 | 120+150+300+400 | PILC+XLPE | 2024-11-29 17:51:08.000000 UTC | 2024-11-29 17:51 | 11 | 4 | 38 | 2024-12-02 23:01:13.000000 UTC | 74 | 0 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 7 | 1 | RYB phase faulty at a distance of 62 meters from Mohan Bakery Substation Switch Number 19780 . Fault pinpointed OPP. RBL BANK NEAR PLOT NO.B43 BOARD. Shown to jJANARDAN. Total length 550 meter. |  | SYSTEM NORMALIZE | 23 | Straight Joint Faulty |  | Fault Details |  | WINTER | 87 | 11:35:00 | 50 | 0.57 | 30.95 | 1481 | 0 | 29.51 | 2024-12-02 18:44:38.000000 UTC | AMBIVLI REC-STN | 2024-11-29 19:00:16.000000 UTC | Section
1000 |  | 11 KV | CRITICAL | MADHUBAN NO. 2 | 32174 | ANTHONY ROAD | 9566 | 300 | XLPE | 2024-11-17 14:12:00.000000 UTC | 2024-11-17 14:12 | 11 | 4 | 50 | 2024-11-19 14:39:04.000000 UTC | 100 | 60 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 4 | 5 | B phase faulty at a distance of 519 meters from Anthony Road Sub Station Switch Number 9566 . Fault pinpointed SUN VILLE BUILDING ON PALIMALA RD . Shown to SHARAD. Total length 704 meter. |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | WINTER | 123 | 90 | 90 | 0.73 | 34.8 | 1543 | 0 | 40.33 | 2024-11-18 19:12:05.000000 UTC | BANDRA REC-STN | 2024-11-17 14:26:07.000000 UTC | Section
5000 |  | 11 KV | CRITICAL | SHRI NIDHI | 16997 | AVENUE SUPERMART | 31989 | 240+300 | PILC+XLPE | 2024-11-17 04:40:00.000000 UTC | 2024-11-17 04:40 | 11 | 8 | 50 | 2024-11-22 23:38:39.000000 UTC | 53 | 10 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 2 | 7 | Y Phase Faulty at 270 Meters from AVENUE SUPERMART Fault Pinpointed at FAULT AT THE CENTRE OF THE ROAD AT THE JUNCTION OF HATKESH AND MIRA BHYANDER ROAD. Total length : 1105 Meters. |  |  | 19 | Transition Joint Faulty |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | WINTER | 66 | 36 | 36 | 0.55 | 34.8 | 1538 | 0 | 40.33 |  | GHODBUNDER REC-STN | 2024-11-17 05:27:31.000000 UTC | Section
4000 |  | 11 KV | MODERATE | DAHISAR WEST REC-STN | 40721 | KUMKUM APARTMENT | 18251 | 300+400 | XLPE | 2024-11-12 11:54:00.000000 UTC | 2024-11-12 11:54 | 11 | 1 | 55 | 2024-11-13 09:52:48.000000 UTC | 41 | 41 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 0 | R Phase Faulty at 46 Meters from KUMKUM APARTMENT Fault Pinpointed at R PHASE FAULTY AT A DISTANCE OF 46 MTR FROM KUMKUM APPT. FAULT PINPOINTED NEAR BHARUCHA DAIRY ON YASHWANT RAO TAWDE ROAD,TOTAL LENGTH 982 MTR,SHOWN TO SANTOSH. Total length : 982 Meters. |  |  | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 60 | 15:00:00 | 50 | 0.83 | 33.64 | 1670 | 0 | 34.36 |  | DAHISAR WEST REC-STN | 2024-11-12 14:58:12.000000 UTC | Section
6000 | POWAI | 11 KV | MODERATE | HIRANANDANI REC-STN | 26373 | LARSEN & TOUBRO | 31233 | 400 | XLPE | 2024-11-12 16:32:00.000000 UTC | 2024-11-12 16:32 | 11 | 1 | 55 | 2024-11-14 21:54:10.000000 UTC | 126 | 126 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 0 | B phase faulty at a distance of 2169 meters from Larsen Sub Station Switch Number 31233 . Fault pinpointed OFF JVLR RD , NEAR POWAI FORTUNE SOCIETY , NEAR SHANKAR TEA STALL. Shown to ANJYA . Total length 3350 meter. |  | SYSTEM NORMALIZE | 4 | Fault Bypassed |  | Fault Details |  | WINTER | 143 | 09:39:00 | 98 | 0.69 | 33.64 | 1670 | 0 | 37 | 2024-11-14 20:46:59.000000 UTC | HIRANANDANI REC-STN | 2024-11-12 17:59:54.000000 UTC | Section
6000 | POWAI | 33 KV | CRITICAL | 220 kV AAREY EHV STATION | 220AAR41 | NAHAR SHAKTI REC-STN | 33207 | 400 | XLPE | 2024-11-12 18:18:00.000000 UTC | 2024-11-12 18:18 | 11 |  | 55 | 2024-11-15 01:30:35.000000 UTC | 125 |  |  |  | NO EXCAVATION ALONG THE ROUTE | 1 |  | R phase faulty at a distance of 795 meters from Nahar Shakti R/S Switch Number 33207 . Fault pinpointed ON DP 9 ROAD NEAR BUDHHA VIHAR OPPSITE BANIYAN TREE . Shown to DILIP. Total length 4190 meter. |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details | 33kV Cable fault | [9 empty] | 2024-11-13 19:51:42.000000 UTC | 220 kV AAREY EHV STATION | 2024-11-12 20:23:36.000000 UTC | Incommer Line
1000 |  | 11 KV | CRITICAL | LAXMI NARAYAN KRUPA | 35936 | SUMANGAL APARTMENT | 43145 | 225+240+300 | PILC+XLPE | 2024-11-12 13:22:00.000000 UTC | 2024-11-12 13:22 | 11 | 8 | 55 | 2024-11-13 16:04:13.000000 UTC | 152 | 80 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 3 | 5 | Y phase faulty at a distance of 120 meters from Laxmi Narayan Krupa Sub Station Switch Number 35936 . Fault pinpointed IN FRONT OF LANDMARK CHS ON BAPUBHAI VASI ROAD. Shown to ANJAIYA. Total length 510 meter. |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details | PRIME AREA | WINTER | 164 | 11:01:00 | 120 | 0.73 | 33.26 | 1694 | 0 | 33.76 | 2024-11-12 22:04:06.000000 UTC | JUHU REC-STN | 2024-11-12 13:41:17.000000 UTC | Section
5000 |  | 11 KV | CRITICAL | SANKALP ENCLAVE | 38856 | MASACHA PADA NO. 2 | 42497 | 300 | XLPE | 2024-09-19 07:59:00.000000 UTC | 2024-09-19 07:59 | 9 | 8 | 109 | 2024-09-27 23:55:38.000000 UTC | 105 | 30 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 3 | 5 | Fault Pinpointed at B phase faulty at a distance of 8 meters from MASACHAPADA 2 S/S . Fault pinpointed NEAR SUBSTATION ON MASACHAPADA ROAD . Shown to SHANKAR . Total length meter 358 MTRS . |  | SYSTEM NORMALIZE | 4 | Fault Bypassed |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | MONSOON | 160 | 16:57:00 | 125 | 0.78 | 31.79 | 1787 | 0 | 44.37 | 2024-10-01 20:33:14.000000 UTC | GHODBUNDER REC-STN | 2024-09-19 09:35:06.000000 UTC | Section
7000 |  | 11 KV | CRITICAL | REPUBLIC | 4365 | GULMARG | 29358 | 225+300 | PILC+XLPE | 2024-09-19 15:19:47.000000 UTC | 2024-09-19 15:20 | 9 | 8 | 109 | 2024-09-23 17:30:05.000000 UTC | 159 | 30 | 0 | 0 | EXCAVATION ALONG THE ROUTE |  | 2 |  |  |  | 22 | Cable Damaged |  | Fault Details | LOAD CURTAILMENT FOR (N-2) SYSTEM | MONSOON | 178 | 11:34:00 | 143 | 0.8 | 31.17 | 1787 | 0 | 44.37 |  | CHUNABHATTI REC-STN | 2024-09-19 16:24:03.000000 UTC | Section
5000 |  | 11 KV | MODERATE | MIRA (M I D C) | 11982 | PERMANENT MAGNET NO 2 | 26953 | 300 | XLPE | 2024-09-19 21:46:00.000000 UTC | 2024-09-19 21:46 | 9 | 3 | 109 | 2024-09-23 02:29:08.000000 UTC | 146 | 110 | 30 | 0 | NO EXCAVATION ALONG THE ROUTE | 4 | 2 | Y Phase Faulty at 228 Meters from MIRA (M I D C) Fault Pinpointed at 6M AWAY FROM PERMANENT MAGNET COMPANY COMPOUND WALL OPP TO STREET LIGHT POLE NO.XSV002/035 NEAR TATA LT PILLAR Total length : 339 Meters. |  |  | 1 | Running Cable Fault |  | Fault Details |  | MONSOON | 173 | 19:50:00 | 140 | 0.81 | 31.79 | 1787 |  | 44.37 |  | MIRA REC-STN | 2024-09-19 23:33:53.000000 UTC | Section
7000 | CHEMBUR | 33 KV | CRITICAL | 220 kV AAREY EHV STATION | 220AAR90 | HINGWALA LANE REC-STN | 33163 | 400 | XLPE | 2024-09-19 15:09:18.000000 UTC | 2024-09-19 15:09 | 9 |  | 109 | 2024-09-23 23:32:49.000000 UTC | 160 |  |  |  | NO EXCAVATION ALONG THE ROUTE | 9 |  | Y Phase Faulty at 4450 Meters from 220 kV AAREY EHV STATION Fault Pinpointed at ON HIRANANDANI VIK LINK ROAD ( TATA POWER ROAD ) ,14 MTR FROM STREET LIGHT POLE NO. SGF018/075 TOWARDS HIRANANDANI HODPITAL . Total length : 9890 Meters. |  |  | 23 | Straight Joint Faulty |  | Fault Details | 33kV Cable fault | [10 empty] | 220 kV AAREY EHV STATION | 2024-09-19 15:25:49.000000 UTC | Incommer Line
1000 | VANDRE | 33 KV | CRITICAL | TATA''S DHARAVI REC-STN | T33DHAOG5H08 | MAKERS REC-STN | 33248 | 400 | XLPE | 2024-10-13 01:36:00.000000 UTC | 2024-10-13 01:36 | 10 |  | 85 | 2024-10-16 09:18:46.000000 UTC | 52 |  |  |  | NO EXCAVATION ALONG THE ROUTE | 5 |  | R Phase Faulty at 2880 Meters from MAKERS REC-STN Fault Pinpointed at Fault pinpointed NEAR SANSAR HOTEL OPPOSITE SALMAN SWEETS, ON 90FT ROAD. Shown to NARSIMHA . Total length meter. |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details | 33kV Cable fault | [9 empty] | 2024-10-14 00:07:33.000000 UTC | TATA''S DHARAVI REC-STN | 2024-10-13 01:53:58.000000 UTC | Incommer Line
1000 | VANDRE | 22 KV | CRITICAL | TATA''S DHARAVI REC-STN | T22DHAOG07H09 | BANDRA TERMINUS REC-STN | 33154 | 300+400 |  | 2024-10-13 03:26:21.000000 UTC | 2024-10-13 03:26 | 10 |  | 85 | 2024-10-16 07:48:29.000000 UTC | 105 |  |  |  | NO EXCAVATION ALONG THE ROUTE | 40 |  | Y Phase Faulty at 4480 Meters from BANDRA TERMINUS REC-STN Fault Pinpointed at Fault pinpointed ON MAHARSHI VALMIKI RD, IN FRONT OF NATIONAL GENERAL STORE. Total length : 4690 Meters. |  | SYSTEM NORMALIZE | 23 | Straight Joint Faulty |  | Fault Details | 22kV Cable fault | [9 empty] | 2024-10-17 10:33:23.000000 UTC | TATA''S DHARAVI REC-STN | 2024-10-13 03:29:29.000000 UTC | Incommer Line
1000 |  | 11 KV | MODERATE | JUHU SCHEME NO.2 | 31723 | V M ROAD NO.1 | 19317 | 300 | XLPE | 2024-10-18 17:50:57.000000 UTC | 2024-10-18 17:51 | 10 | 7 | 80 | 2024-10-21 19:34:11.000000 UTC | 123 | 0 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE |  | 0 | Y Phase Faulty at 32 Meters from V M ROAD NO.1 Fault Pinpointed at on CENTRE OF V M RD & NEAR METRO PILLAR.. Shown to SHARAD. Total length meter. |  | SYSTEM NORMALIZE | 4 | Fault Bypassed |  | Fault Details |  | MONSOON | 163 | 23:32:00 | 140 | 0.86 |  |  |  |  | 2024-10-20 04:56:32.000000 UTC | JUHU REC-STN | 2024-10-18 19:04:28.000000 UTC | Section
4000 |  | 11 KV | MODERATE | JAIN TEMPLE | 17452 | BORIVALI RESERVOIR | 10400 | 120 | PILC | 2024-10-18 18:10:00.000000 UTC | 2024-10-18 18:10 | 10 | 4 | 80 | 2024-10-21 01:39:48.000000 UTC | 45 | 5 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 9 | 3 | Fault Pinpointed at B phase faulty at a distance of 980 meters from Borivli Reservoir Sub Station Switch Number . Fault pinpointed 5 MTRS FROM SANJAY GANDHI NATIONAL PARK BOARD . Shown to MANGESH . Total length 2100 meter. |  |  | 23 | Straight Joint Faulty |  | Fault Details |  | MONSOON | 52 | 23:07:00 | 40 | 0.77 |  | 1979 |  |  |  | BORIVALI REC-STN | 2024-10-18 21:23:52.000000 UTC | Section
1000 |  | 11 KV |  | MANI PADA NO.1 | 42737 | UNIVERSITY CAMPUS NO.1 | 9893 |  |  | 2024-10-04 10:10:00.000000 UTC | 2024-10-04 10:10 | 10 |  | 94 | 2024-10-06 11:55:34.000000 UTC | [9 empty] | SYSTEM NORMALIZE | 22 | Cable Damaged |  | Fault Details |  | MONSOON | 163 | 12:09:00 | 131 | 0.8 |  |  |  |  | 2024-10-04 17:49:53.000000 UTC | KALINA REC-STN | 2024-10-04 11:08:34.000000 UTC | Section
6000 |  | 11 KV | CRITICAL | VIKHROLI REC-STN | 7832 | GHATKOPAR ARIHANT | 42822 | 240+300 | PILC+XLPE | 2024-10-04 18:34:56.000000 UTC | 2024-10-04 18:35 | 10 | 1 | 94 | 2024-10-06 03:12:30.000000 UTC | 86 | 86 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 3 | 5 | B Phase Faulty at 205 Meters from FORTH RD Fault Pinpointed at near shankar mandir in frant of meter cabin on bannien tree Total length : 700 Meters. |  | SYSTEM NORMALIZE | 19 | Transition Joint Faulty |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | MONSOON | 101 | 14:34:00 | 65 | 0.64 | 33.38 | 1896 | 0 | 44.39 | 2024-10-06 03:20:12.000000 UTC | VIKHROLI REC-STN | 2024-10-04 18:39:19.000000 UTC | Section
3000 |  | 11 KV | MODERATE | JANU PADA | 10547 | DRUG HOUSE | 14546 | 300 | XLPE | 2024-10-04 05:48:00.000000 UTC | 2024-10-04 05:48 | 10 | 2 | 94 | 2024-10-05 23:21:49.000000 UTC | 96 | 80 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 18 | 2 | Fault Pinpointed at Y phase faulty at a distance of 347 meters from Drug House Substation Switch Number 14546 . Fault pinpointed BELOW AKURLI ROAD SUBWAY . Shown to MR.REDDY . Total length 480 meter. |  |  | 4 | Fault Bypassed |  | Fault Details | LOAD CURTAILMENT FOR (N-2) SYSTEM | WINTER | 145 | 11:27:00 | 110 | 0.76 | 33.38 | 1896 | 0 | 44.39 |  | TIMES OF INDIA REC-STN | 2024-10-04 08:19:45.000000 UTC | Section
2000 |  | 11 KV | CRITICAL | TANDICE 69 | 43020 | BOSTON NO-2 | 35731 | 300 | XLPE | 2024-11-25 12:52:00.000000 UTC | 2024-11-25 12:52 | 11 | 4 | 42 | 2024-11-26 20:43:45.000000 UTC | 117 | 65 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 6 | R phase faulty at a distance of 113 meters from Boston No 2 Substation Switch Number 35731 . Fault pinpointed FRONT OF DARPAN TELEPHONE EXCHANGE.. Shown to GAWADE. Total length 239 meter. |  |  | 1 | Running Cable Fault |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | WINTER | 114 | 14:01:00 | 56 | 0.49 | 31.55 | 1559 | 0 | 30.95 |  | CHAKALA REC-STN | 2024-11-25 15:36:49.000000 UTC | Section
3000 |  | 11 KV | CRITICAL | UDYOG NAGAR NO.1 | 13606 | KRISHNA COMMERCIAL CENTER | 19740 | 120 | PILC | 2024-11-25 11:51:00.000000 UTC | 2024-11-25 11:51 | 11 | 6 | 42 | 2024-11-28 23:29:10.000000 UTC | 125 | 0 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 8 | YB Phase Faulty at 120 Meters from UDYOG NAGAR NO.1 Fault Pinpointed at 10 MTR FROM KRISHNA COMMERCIAL GATE Total length : 208 Meters. |  |  | 1 | Running Cable Fault |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | WINTER | 140 | 11:20:00 | 120 | 0.86 | 31.55 | 1559 | 0 | 30.95 |  | MIND SPACE REC-STN | 2024-11-25 12:45:54.000000 UTC | Section
3000 | MALAD | 11 KV | MODERATE | MALVANI COLONY NO.5 | 14606 | MALWANI MHADA PUMP | 18331 | 300 | XLPE | 2024-11-25 21:19:00.000000 UTC | 2024-11-25 21:19 | 11 | 2 | 42 | 2024-11-27 07:29:57.000000 UTC | 111 | 70 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 7 | 0 |  |  |  | 22 | Cable Damaged |  | Fault Details |  | WINTER | 148 | 104 | 104 | 0.7 | 31.55 | 1559 | 0 | 3095 |  | PALM COURT REC-STN | 2024-11-25 22:28:52.000000 UTC | Section
4000 |  | 11 KV | CRITICAL | BHAGWATI HOSPITAL NO 2 |  | LIC COLONY NO 1 |  | 120+300 | PILC+XLPE | 2024-10-11 12:41:00.000000 UTC | 2024-10-11 12:41 | 10 | 6 | 87 | 2024-10-12 23:18:57.000000 UTC | 45 | 0 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 2 | 3 |  |  | SYSTEM NORMALIZE | 22 | Cable Damaged |  | Fault Details | SUBSTATIONS ARE AFFECTED | MONSOON | 100 | 75 | 75 | 0.75 | 34.53 |  |  | 46.45 | 2024-10-16 08:25:46.000000 UTC | DEVIDAS LANE REC-STN | 2024-10-12 01:32:33.000000 UTC | Section
4000 |  | 11 KV | MODERATE | DAHISAR CHECKPOST | 15464 | TIMBER GREEN HOMES | 28047 | 300+400 | XLPE | 2024-10-11 17:48:01.000000 UTC | 2024-10-11 17:48 | 10 | 3 | 87 | 2024-10-14 23:34:28.000000 UTC | 94 | 10 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 1 | 2 | B phase faulty at a distance of 464 meters from Timber Green Homes Substation Switch Number 28047 . Fault pinpointed NEAR DAHISAR CHECKNAKA BUS STOP, NEAR SIGNAL POLE NO. 10. Shown to NARESH. Total length 700 meter. |  |  | 1 | Running Cable Fault |  | Fault Details |  | MONSOON | 103 | 10:29:00 | 89 | 0.86 | 34.53 |  | 2.5 | 46.45 |  | DAHISAR CHECKNAKA REC-STN | 2024-10-11 18:02:46.000000 UTC | Section
1000 |  | 11 KV | MODERATE | JOY RESIDENCY | 32830 | SPAN CENTRE | 14104 | 240+300 | PILC+XLPE | 2024-10-11 17:05:05.000000 UTC | 2024-10-11 17:05 | 10 | 10 | 87 | 2024-10-15 07:31:58.000000 UTC | 105 | 15 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 1 | 2 | R phase faulty at a distance of 353 meters from Span Centre Sub Station Switch Number 32830 . Fault pinpointed NEAR DRAINAGE CHAMBER & 2M FROM SATYA SAI DARSHAN CHAWK. Shown to GOPI & ASHOK. Total length 570 meter. |  |  | 4 | Fault Bypassed |  | Fault Details |  | MONSOON | 117 | 20:49:00 | 98 |  | 34.53 | 1832 | 2.5 | 46.45 |  | BANDRA REC-STN | 2024-10-11 17:34:39.000000 UTC | Section
3000 |  | 11 KV | MODERATE | MALAD REC-STN | 18444 | PRAGATI SHOPPING | 11086 | 240+300+400 | PILC+XLPE | 2024-10-11 10:54:00.000000 UTC | 2024-10-11 10:54 | 10 | 1 | 87 | 2024-10-14 12:01:43.000000 UTC | 67 | 67 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 14 | 0 | RYB Phase Faulty at 735 Meters from MALAD REC-STN Fault Pinpointed at IN MALAD SUBWAY Total length : 1150 Meters. |  |  | 19 | Transition Joint Faulty |  | Fault Details |  | MONSOON | 74 | 11:40:00 | 64.5 | 0.87 | 34.53 | 1847 | 0 | 46.45 |  | MALAD REC-STN | 2024-10-11 11:55:17.000000 UTC | Section
3000 |  | 11 KV | CRITICAL | GOREGAON EAST NO.3 | 36595 | NAIKWADI RONIT | 41371 | 300 | XLPE | 2024-10-11 12:56:00.000000 UTC | 2024-10-11 12:56 | 10 | 5 | 87 | 2024-10-14 16:24:02.000000 UTC | 197 | 80 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 1 | 8 | Fault Pinpointed at B PHASE FAULTY AT A DISTANCE 188 MTRS FROM GOREGAON EAST NO 3 , FAULT PINPOINTED ON AAREY ROAD NEAR ANUPUM THEATRE GATE , SHOWN TO LINGAYA , TOTAL LENGTH 661 MTRS |  |  | 1 | Running Cable Fault |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | MONSOON | 226 | 11:47:00 | 138 | 0.61 | 34.53 | 1832 | 0 | 46.45 |  | NIRLON REC-STN | 2024-10-11 13:45:17.000000 UTC | Section
5000 |  | 11 KV | MODERATE | PARAG NAGAR | 17773 | ROYAL PARK | 16150 | 240+300+400 | PILC+XLPE | 2024-12-03 10:22:00.000000 UTC | 2024-12-03 10:22 | 12 | 1 | 34 | 2024-12-06 07:36:33.000000 UTC | 80 | 80 | 0 | 0 | EXCAVATION ALONG THE ROUTE |  | 2 |  |  |  | 22 | Cable Damaged |  | Fault Details |  | WINTER | 84 | 10:07:00 | 40 | 0.48 | 41.39 | 1683 | 0 | 33.42 |  | MIRA REC-STN | 2024-12-03 11:58:09.000000 UTC | Section
7000 |  | 11 KV | MODERATE | PANT NGR EMBASSY | 42432 | M.G.RD 5 | 9332 | 120+150 | XLPE | 2024-12-03 11:58:00.000000 UTC | 2024-12-03 11:58 | 12 | 1 | 34 | 2024-12-06 23:51:31.000000 UTC | 70 | 70 | 0 | 0 | EXCAVATION ALONG THE ROUTE |  | 0 | R Phase Faulty at 351 Meters from BHAGATSINGH NAGAR NO.2 Fault Pinpointed at FPP OPPOSITE G SQUARE BUILDING GATE Total length : 1684 Meters. |  | SYSTEM NORMALIZE | 4 | Fault Bypassed |  | Fault Details |  | WINTER | 92 | 10:17:00 | 50 | 0.54 |  |  | 0 |  | 2024-12-06 22:04:52.000000 UTC | HINGWALA LANE REC-STN | 2024-12-03 13:53:29.000000 UTC | Section
4000 |  | 11 KV | MODERATE | DAHISAR REC-STN | 11763 | DAHISAR WEST NO.3 | 9515 | 240+300 | PILC+XLPE | 2024-12-03 05:44:00.000000 UTC | 2024-12-03 05:44 | 12 | 1 | 34 | 2024-12-06 06:47:43.000000 UTC | 19 | 19 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE |  | 3 | B Phase Faulty at 224 Meters from DAHISAR REC-STN Fault Pinpointed at OPP FIRE BRIGADE OFFICE Total length : 834 Meters. |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 57 | 35 | 35 | 0.61 | 33.42 | 1617 | 0 | 41.39 | 2024-12-04 18:52:02.000000 UTC | DAHISAR REC-STN | 2024-12-03 06:46:30.000000 UTC | Section
4000 |  | 11 KV | MODERATE | SONAL | 16128 | IC COLONY NO 2 | 12653 | 300 | XLPE | 2024-12-03 10:05:00.000000 UTC | 2024-12-03 10:05 | 12 | 2 | 34 | 2024-12-05 07:36:25.000000 UTC | 71 | 61 | 0 | 0 | EXCAVATION ALONG THE ROUTE |  | 2 | RY phase faulty at a distance of 115 meters from Sonal Sub Station Switch Number 16128 . Fault pinpointed ON IC COLONY ROAD OPPO RAHUL OPTICAL DORA ROSE BLDG. Shown to NARESH. Total length 300 meter. |  |  | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 96 | 18:30:00 | 62 | 0.65 | 41.39 | 1683 | 0 | 33.42 |  | DEVIDAS LANE REC-STN | 2024-12-03 11:55:31.000000 UTC | Section
5000 |  | 11 KV | MODERATE | SHIVDARSHAN BUILDING | 34772 | EDEN ROSE | 17132 | 300 | XLPE | 2024-12-03 22:19:40.000000 UTC | 2024-12-03 22:20 | 12 | 3 | 34 | 2024-12-06 07:36:33.000000 UTC | 113 | 100 | 0 | 1 | NO EXCAVATION ALONG THE ROUTE |  | 3 | Fault Pinpointed at B PHASE FAULTY AT A DIST OF 304 MTRS FROM EDEN ROSW FPP IN FRONT EDEN ROSE NEAR LT PILLAR 34120202 TOTAL LENGTH 3366 MTRS SHOEN TO SANTOSH |  | SYSTEM NORMALIZE | 23 | Straight Joint Faulty |  | Fault Details |  | WINTER | 117 | 22:03:00 | 70 | 0.6 | 33.42 | 1683 | 0 | 41.39 | 2024-12-06 19:40:06.000000 UTC | SADGURU REC-STN | 2024-12-03 23:51:36.000000 UTC | Section
3000 |  | 11 KV | CRITICAL | DOMNIC COLONY EROS | 39392 | ORLEM TANK ROAD NO.1 | 14840 | 300 | XLPE | 2024-10-24 15:45:00.000000 UTC | 2024-10-24 15:45 | 10 | 9 | 74 | 2024-10-28 16:30:31.000000 UTC | 154 | 27 | 0 | 1 | EXCAVATION ALONG THE ROUTE | 1 | 2 | R phase faulty at a distance of 70 meters from Orlem Tank Road No.1 Substation Switch Number 14840 . Fault pinpointed ORLEM TANK ROAD ROAD OPPO SHILPA BEAUTY PARLOUR.. Shown to LINGYAH. Total length 215 meter. |  | SYSTEM NORMALIZE | 4 | Fault Bypassed |  | Fault Details |  | WINTER | 162 | 121 | 121 | 0.75 | 35.59 | 1957 | 0.46 | 46.48 | 2024-10-25 20:47:15.000000 UTC | MALAD REC-STN | 2024-10-24 16:03:53.000000 UTC | Section
1000 |  | 11 KV | CRITICAL | OPULANCE | 34964 | PANDIT NEHRU ROAD NO.2 | 4131 | 240+300 | PILC+XLPE | 2024-10-24 21:27:58.000000 UTC | 2024-10-24 21:28 | 10 | 7 | 74 | 2024-10-30 01:37:48.000000 UTC | 77 | 0 | 0 | 1 | NO EXCAVATION ALONG THE ROUTE | 3 | 6 | Y Phase Faulty at 200 Meters from PANDIT NEHRU ROAD NO.2 Fault Pinpointed at ON THE TPC SCENE ROAD 7, SANTACRUZ STATION ROAD JUNCTION, IN FRONT OF RADHA KRISHNA HOTEL, NEAR TO CCTV POLE BOX VAK5708 Total length : 353.6 Meters. |  |  | 19 | Transition Joint Faulty |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | MONSOON | 80 | 50 | 50 | 0.63 | 35.59 | 1957 | 0 | 46.48 |  | SARASWATI RD. REC-STN | 2024-10-24 21:30:02.000000 UTC | Section
1000 | VANDRE | 33 KV | CRITICAL | TATA''S DHARAVI REC-STN | T33DHAOG6H08 | BANDRA REC-STN | 33325 | 400 | XLPE | 2024-10-23 01:09:00.000000 UTC | 2024-10-23 01:09 | 10 |  | 75 | 2024-10-24 05:09:50.000000 UTC | 198 |  |  |  | NO EXCAVATION ALONG THE ROUTE | 23 |  | R Phase Faulty at 1650 Meters from BANDRA REC-STN Fault Pinpointed at WESTERN EXPRESS HIGHWAY NEAR BANDRA EAST KALANAGAR SIDE 10MTR FROM STREET LIGHT POLE NO EWH002/001 AND 3 MTR FROM WALL. |  |  | 23 | Straight Joint Faulty |  | Fault Details | 33kV Cable fault | [10 empty] | TATA''S DHARAVI REC-STN | 2024-10-23 02:47:03.000000 UTC | Incommer Line
1000 | VANDRE | 33 KV | CRITICAL | TATA''S DHARAVI REC-STN | T33DHAOG9H24 | PALI REC-STN | 33236 | 400 | XLPE | 2024-10-22 23:04:00.000000 UTC | 2024-10-22 23:04 | 10 |  | 76 | 2024-10-23 05:08:54.000000 UTC | 216 |  |  |  | NO EXCAVATION ALONG THE ROUTE | 16 |  | Y Phase Faulty at 2700 Meters from PALI REC-STN Fault Pinpointed at WESTERN EXPRESSWAY HIGHWAY AT 30MTR FROM POLE NO 002/001 . |  |  | 23 | Straight Joint Faulty |  | Fault Details | 33kV Cable fault | [10 empty] | TATA''S DHARAVI REC-STN | 2024-10-23 00:49:11.000000 UTC | Incommer Line
1000 | VANDRE | 22 KV |  | TATA''S DHARAVI REC-STN | T22DHAOG07H09 | BANDRA TERMINUS REC-STN | 33154 |  |  | 2024-10-07 02:49:37.000000 UTC | 2024-10-07 02:50 | 10 |  | 91 | [8 empty] | B Phase Faulty at 4400 Meters from BANDRA TERMINUS REC-STN Fault Pinpointed at S.K CUTILERY STORE SHOP NO.27 TATARIA RD EXACT OPPOSITE OF SHITLA DEVI MANDIR,DHARAVI. Total length : 4700 Meters. |  |  | 19 | Transition Joint Faulty |  | Fault Details | [11 empty] | BANDRA TERMINUS REC-STN | 2024-10-07 10:11:08.000000 UTC | Incommer Line
6000 |  | 11 KV | MODERATE | EVEREST NO.2 | 34884 | HILL VIEW 2 | 15536 | 185+240+300 | PILC+XLPE | 2024-10-07 15:20:00.000000 UTC | 2024-10-07 15:20 | 10 | 5 | 91 | 2024-10-08 02:34:55.000000 UTC | 109 | 109 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 7 | 4 | Y Phase Faulty at 320 Meters from EVEREST NO.2 Fault Pinpointed at NEAR NORTHEN ZYKA HOTEL OR MATOSHRI MEDICAL ON LBS MARG Total length : UPPAN Meters. |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details |  | MONSOON | 135 | 12:07:00 | 92 | 0.68 | 35.61 | 1961 | 0 | 53.46 | 2024-10-09 00:13:59.000000 UTC | HCC REC-STN | 2024-10-07 16:52:04.000000 UTC | Section
1000 |  | 11 KV | CRITICAL | JUHU REC-STN | 28484 | N.S. ROAD NO. 4 | 38643 | 240+300 | PILC+XLPE | 2024-10-07 12:28:00.000000 UTC | 2024-10-07 12:28 | 10 | 1 | 91 | 2024-10-09 14:53:42.000000 UTC | 110 | 110 |  | 0 | NO EXCAVATION ALONG THE ROUTE |  | 5 |  |  |  | 19 | Transition Joint Faulty |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | SUMMER | 114 | 11:45:00 | 89 | 0.78 |  |  | 0 |  |  | JUHU REC-STN | 2024-10-07 13:10:48.000000 UTC | Section
3000 |  | 11 KV | MODERATE | MALAD REC-STN | 29559 | BANDONGRI ROAD WEST | 13879 | 225+300 | PILC+XLPE | 2024-12-01 08:04:00.000000 UTC | 2024-12-01 08:04 | 12 | 1 | 36 | 2024-12-04 15:01:29.000000 UTC | 47 | 47 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 4 | 0 |  |  |  | 22 | Cable Damaged |  | Fault Details |  | WINTER | 80 | 09:40:00 | 60 | 0.75 | 32.08 | 1257 | 0 | 32.96 |  | MALAD REC-STN | 2024-12-01 09:21:08.000000 UTC | Section
4000 |  | 11 KV | CRITICAL | VISHWAGANGA | 34270 | BHAGWATI HOSPITAL | 30903 | 300 | XLPE | 2024-12-01 12:12:00.000000 UTC | 2024-12-01 12:12 | 12 | 2 | 36 | 2024-12-04 22:39:38.000000 UTC | 37 | 30 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 3 | 8 | Fault Pinpointed at R PHASE FAULTY AT A DISTANCE OF 374 MTRS FROM VISHWAGANGA S/S FPP IN BHAGWATI HOSP COMPOUND SHOWN TO SANTOSH TOTAL LENGTH 440 MTRS |  |  | 1 | Running Cable Fault |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | WINTER | 48 | 10:25:00 | 30 | 0.63 | 32.08 | 1257 | 0 | 32.96 |  | DEVIDAS LANE REC-STN | 2024-12-01 12:51:38.000000 UTC | Section
5000 | MIRA BHAINDER | 33 KV | CRITICAL | 220kV GHODBUNDER REC-STN | 220GHO47 | SHANTI STAR MIRA REC-STN | 33176 | 400 | XLPE | 2024-12-01 04:40:00.000000 UTC | 2024-12-01 04:40 | 12 |  | 36 | 2024-12-04 05:22:42.000000 UTC | 69 |  |  |  | NO EXCAVATION ALONG THE ROUTE |  |  | R Phase Faulty at 662 Meters from SHANTI STAR MIRA REC-STN Fault Pinpointed at NEAR SRUSHTI ROAD JUNCTION OF AYAPPA TEMPLE Total length : 4839 Meters. |  |  | 4 | Fault Bypassed |  | Fault Details | 33kV Cable fault | [10 empty] | 220kV GHODBUNDER REC-STN | 2024-12-01 05:16:41.000000 UTC | Incommer Line
7000 |  | 11 KV | MODERATE | BORLA SOC | 36806 | TOLARAM NGR | 6966 | 240+300 | PILC+XLPE | 2024-09-17 19:35:52.000000 UTC | 2024-09-17 19:36 | 9 | 2 | 111 | 2024-09-22 23:27:43.000000 UTC | 82 | 50 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 1 | 2 | Y Phase Faulty at 780 Meters from BORLA SOC Fault Pinpointed at on cg gidwani rd near lt pillar no 07130309 Total length : 888 Meters. |  | SYSTEM NORMALIZE | 19 | Transition Joint Faulty |  | Fault Details |  | MONSOON | 98 | 22:23:00 | 70 | 0.71 | 32.7 | 1633 | 0.5 | 42.12 | 2024-09-22 22:04:16.000000 UTC | CHEMBUR REC-STN | 2024-09-17 20:18:02.000000 UTC | Section
4000 |  | 11 KV | MODERATE | JAIN TEMPLE | 17452 | BORIVALI RESERVOIR | 10400 | 120 | PILC | 2024-09-17 03:47:00.000000 UTC | 2024-09-17 03:47 | 9 | 4 | 111 | 2024-09-20 04:31:20.000000 UTC | 42 | 5 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE |  | 3 | B phase faulty at a distance of 823 meters from Borivli Reservoir Sub Station Switch Number 10400 . Fault pinpointed 6M WEST SIDE AT THE CORNER OF KENERI CAVES ROAD AND BMC COLONY ROAD.. Shown to PALANI. Total length 1609 meter. |  |  | 1 | Running Cable Fault |  | Fault Details |  | MONSOON | 48 | 19:10:00 | 34 | 0.71 | [5 empty] | BORIVALI REC-STN | 2024-09-17 04:27:04.000000 UTC | Section
2000 |  | 11 KV | CRITICAL | QUTUBI MANZIL | 28084 | MAROL WEST NO.2 | 16690 | 120+150 | PILC+XLPE | 2024-11-22 14:36:00.000000 UTC | 2024-11-22 14:36 | 11 | 10 | 45 |  | 56 | 15 | 0 | 0 | EXCAVATION ALONG THE ROUTE |  | 3 |  | CABLE DAMAGED IN FRONT OF QUTUBI MANZIL CSS GATE ON MAROL PIPELINE ROAD BY MCGM(BMC) |  | 22 | Cable Damaged |  | Fault Details | LOAD CURTAILMENT FOR (N-2) SYSTEM | [10 empty] | AAREY 220 KV RECEIVING STATION | 2024-11-22 15:39:29.000000 UTC | Section
5000 |  | 11 KV | CRITICAL | AGARWAL IND EST | 4517 | SUNLITE HEIGHTS | 11358 | 120 | PILC | 2024-11-22 09:35:00.000000 UTC | 2024-11-22 09:35 | 11 | 3 | 45 | 2024-11-23 20:25:29.000000 UTC | 48 | 30 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 2 | 5 |  |  | SYSTEM NORMALIZE | 22 | Cable Damaged |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | WINTER | 66 | 40 | 40 | 0.61 | 33.96 | 1611 | 0 | 33.04 | 2024-11-23 19:50:40.000000 UTC | MIRA REC-STN | 2024-11-22 10:32:59.000000 UTC | Section
4000 |  | 11 KV | MODERATE | RAJ ANMOL TOWER | 15694 | VINI GARDEN | 28470 | 120+150 | PILC+XLPE | 2024-11-22 14:32:00.000000 UTC | 2024-11-22 14:32 | 11 | 2 | 45 | 2024-11-23 20:26:10.000000 UTC | 35 | 30 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 3 |  |  |  | 22 | Cable Damaged |  | Fault Details |  | WINTER | 37 | 22:37:00 | 22 | 0.59 | 33.04 | 1611 | 0 | 33.96 |  | DAHISAR WEST REC-STN | 2024-11-22 15:33:13.000000 UTC | Section
3000 |  | 11 KV | CRITICAL | RAMCHANDRA LANE NO.3 | 39111 | GEMSTAR COMMERCIAL COMPLEX | 29066 | 120+150 | PILC+XLPE | 2024-11-22 14:01:00.000000 UTC | 2024-11-22 14:01 | 11 | 8 | 45 | 2024-11-22 21:49:41.000000 UTC | 164 | 20 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 2 | Y Phase Faulty at 87 Meters from GEMSTAR COMMERCIAL COMPLEX Fault Pinpointed at FP NEAR OPP SIDE OF IDBI BANK ON RAMCHANDRA LANE Total length : 270 Meters. |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details | SUBSTATIONS ARE AFFECTED | WINTER | 193 | 14:47:00 | 162 | 0.84 |  |  | 0 |  | 2024-11-22 21:04:00.000000 UTC | MALAD REC-STN | 2024-11-22 16:08:28.000000 UTC | Section
1000 |  | 11 KV | MODERATE | MOTILAL NEHRU NAGAR NO 2 | 29037 | PINNACLE CORP. PLAZA | 32732 | 300 | XLPE | 2024-10-14 13:38:00.000000 UTC | 2024-10-14 13:38 | 10 | 2 | 84 | 2024-10-17 15:01:01.000000 UTC | 153 | 133 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 2 |  |  |  | 22 | Cable Damaged |  | Fault Details |  | WINTER | 87 | 71 | 71 | 0.82 | 34.25 | 1957 | 0.25 | 50.92 |  | MMRDA REC-STN | 2024-10-14 14:50:43.000000 UTC | Section
5000 |  | 11 KV | MODERATE | NAYA NAGAR NO 1 | 11365 | ASMITA ENCLAVE NO 1 | 12939 | 240 | PILC | 2024-10-09 10:21:00.000000 UTC | 2024-10-09 10:21 | 10 | 4 | 89 | 2024-10-10 07:38:15.000000 UTC | 94 | 45 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 3 | 0 |  |  |  | 22 | Cable Damaged |  | Fault Details |  | MONSOON | 98 | 10:10:00 | 73 | 0.74 | 29.9 | 1907 | 4.25 | 41.98 |  | SHANTI STAR MIRA REC-STN | 2024-10-09 12:52:59.000000 UTC | Section
3000 |  | 11 KV | MODERATE | DINDOSHI VASAHAT CENTRAL | 17143 | DINDOSHI VASAHAT NO.2 | 15478 | 120 | PILC | 2024-10-09 15:08:38.000000 UTC | 2024-10-09 15:09 | 10 | 9 | 89 | 2024-10-10 07:32:38.000000 UTC | 170 | 10 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 3 | 2 | Fault Pinpointed at R&Y PHASE FAULTY AT 58 MTR FROM DINDOSHI VASAT CSS, FAULT PINPOINTED NEAR SULABH SHAUCHALAY, BMC COLONY RD, SANTOSH NGR,TOTAL LENGTH 85 MTR, SHOWN TO LINGYAA |  |  | 4 | Fault Bypassed |  | Fault Details |  | WINTER | 236 | 23:30:00 | 150 | 0.64 | 29.9 | 1907 | 0 | 41.98 |  | RAHEJA I.T. PARK REC-STN | 2024-10-09 16:25:17.000000 UTC | Section
4000 |  | 11 KV | MODERATE | ISCON MIRA | 38339 | PENKARPADA | 37814 | 120+300 | PILC+XLPE | 2024-10-09 10:07:00.000000 UTC | 2024-10-09 10:07 | 10 | 3 | 89 | 2024-10-10 07:51:43.000000 UTC | 136 | 36 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 4 | 4 |  |  | SYSTEM NORMALIZE | 22 | Cable Damaged |  | Fault Details |  | MONSOON | 136 | 09:43:00 | 110 | 0.81 | 29.9 | 1907 | 4.25 | 41.98 | 2024-10-09 21:08:38.000000 UTC | DAHISAR CHECKNAKA REC-STN | 2024-10-09 12:36:38.000000 UTC | Section
5000 | MIRA BHAINDER | 11 KV | MODERATE | RUPANI | 43191 | RAVI MHADA REC-STN | 38215 | 300+400 | XLPE | 2024-12-02 14:14:00.000000 UTC | 2024-12-02 14:14 | 12 | 3 | 35 | 2024-12-06 06:51:08.000000 UTC | 0 | 0 | 0 | 0 | EXCAVATION ALONG THE ROUTE |  | 1 |  |  |  | 22 | Cable Damaged |  | Fault Details |  | WINTER | 0 | 00:00:00 | 0 |  | 34.2 | 1573 |  | 40.68 |  | MIRA REC-STN | 2024-12-02 16:12:46.000000 UTC | Section
4000 |  | 11 KV | CRITICAL | RATAN NAGAR NO 2 | 7501 | RATAN NAGAR NO 1 | 7447 | 300 | XLPE | 2024-12-02 14:18:00.000000 UTC | 2024-12-02 14:18 | 12 | 6 | 35 | 2024-12-07 22:26:10.000000 UTC | 43 | 10 | 30 | 1 | EXCAVATION ALONG THE ROUTE | 1 | 3 |  |  |  | 22 | Cable Damaged |  | Fault Details | LOAD CURTAILMENT FOR (N-2) SYSTEM | WINTER | 145 | 09:52:00 | 110 | 0.76 | 34.2 | 1573 | 0 | 40.68 |  | BORIVALI REC-STN | 2024-12-02 16:08:22.000000 UTC | Section
1000 |  | 11 KV | CRITICAL | MADHUBAN NO. 2 | 32174 | ANTHONY ROAD | 9566 | 300 | XLPE | 2024-10-16 01:09:00.000000 UTC | 2024-10-16 01:09 | 10 | 5 | 82 | 2024-10-16 07:24:50.000000 UTC | 66 | 40 | 0 | 0 | EXCAVATION ALONG THE ROUTE |  | 5 |  |  |  | 22 | Cable Damaged |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | MONSOON | 125 | 12:17:00 | 87 | 0.7 | 33.6 | 1853 | 6 | 44.86 |  | BANDRA REC-STN | 2024-10-16 01:09:50.000000 UTC | Section
2000 |  | 11 KV | MODERATE | MAROL MAROSHI BUS DEPOT | 14333 | WOODLAND ESTATE | 32891 | 240+300 | PILC+XLPE | 2024-12-04 18:06:00.000000 UTC | 2024-12-04 18:06 | 12 | 5 | 33 | 2024-12-08 23:27:02.000000 UTC | 208 | 160 | 100 | 1 | NO EXCAVATION ALONG THE ROUTE | 2 | 1 | Fault Pinpointed at RYB PHASE FAULTY AT THE DISTANCE OF 194 MTR FROM MIDC CENTRAL CSS, FAULT PINPOINTED IN FRONT OF SARASWAT BANK , MIDC CENTRAL RD, SHOWN TO JANARDAN, TOTAL DISTANCE 365 MTR |  |  | 19 | Transition Joint Faulty |  | Fault Details |  | WINTER | 181 | 12:02:00 | 122.5 | 0.68 | 35.39 | 1761 | 0 | 43.72 |  | AAREY 220 KV RECEIVING STATION | 2024-12-04 20:31:28.000000 UTC | Section
7000 |  | 11 KV | CRITICAL | BHIMWADI 2 | 16401 | SHANBAUG STRORAGE | 19699 | 300 | XLPE | 2024-12-04 10:21:00.000000 UTC | 2024-12-04 10:21 | 12 | 5 | 33 | 2024-12-07 02:28:37.000000 UTC | 120 | 50 | 40 | 0 | EXCAVATION ALONG THE ROUTE | 7 | 5 | Fault Pinpointed at b phase faulty at a distance of 765 mtrs from shanbaug storage s/s fpp near masjid on sonapur lane and pl lokhande marg junction oppo nurani sweets shown to narsinha total length 1047 mtrs |  |  | 4 | Fault Bypassed |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | WINTER | 133 | 09:56:00 | 100 | 0.75 | 35.39 | 1761 | 0 | 43.72 |  | NATWAR PAREKH REC-STN | 2024-12-04 15:03:53.000000 UTC | Section
4000 |  | 11 KV | MODERATE | VISHRAMYOG | 11702 | GORAI HOUSING | 6667 | 300 | XLPE | 2024-12-04 14:21:23.000000 UTC | 2024-12-04 14:21 | 12 | 2 | 33 | 2024-12-06 23:55:42.000000 UTC | 71 | 20 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 0 | Y Phase Faulty at 56 Meters from GORAI HOUSING Fault Pinpointed at near corner of the playground opp site of jaywant lokhande cllg. Total length : 486 Meters. |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 86 | 10:32:00 | 67 | 0.78 | 33.42 | 1683 | 0 | 41.39 | 2024-12-06 16:41:02.000000 UTC | VAZIRA REC-STN | 2024-12-04 14:26:23.000000 UTC | Section
6000 | POWAI | 11 KV | CRITICAL | READY MIX CONCRETE PLANT | 19747 | AMARTARA 2 | 38580 | 240+300 | PILC+XLPE | 2024-10-29 15:31:00.000000 UTC | 2024-10-29 15:31 | 10 | 2 | 69 | 2024-11-02 21:57:22.000000 UTC | 122 | 110 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 9 | 2 | RYB Phase Faulty at 634 Meters from READY MIX CONCRETE PLANT Fault Pinpointed at IES SCHOOL PREMISES... Total length : 1670 Meters. |  | SYSTEM NORMALIZE | 23 | Straight Joint Faulty |  | Fault Details |  | WINTER | 122 | 80 | 80 | 0.66 | 32.61 | 1921 | 0 | 49.67 | 2024-10-31 21:55:33.000000 UTC | AAREY 220 KV RECEIVING STATION | 2024-10-29 16:51:15.000000 UTC | Section
4000 |  | 11 KV | MODERATE | LAKSHACHANDI COLOUMBIA | 37538 | OM TOWER | 13447 | 240+300 | PILC+XLPE | 2024-10-29 03:30:00.000000 UTC | 2024-10-29 03:30 | 10 | 7 | 69 | 2024-10-31 04:06:52.000000 UTC | 70 | 10 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 3 | 3 | Fault Pinpointed at RYB phase faulty at a distance of 65 meters from Lakshachandi Coloumbia Substation Switch Number 37538 . Fault pinpointed INFRONT OF MARUTI SUZUKI SHOWROOM NEAR STREET LIGHT POLE NO.WDG/001/090 ON S V ROAD . Shown to NARESH. Total length 485 meter. |  | SYSTEM NORMALIZE | 19 | Transition Joint Faulty |  | Fault Details |  | WINTER | 112 | 14:58:00 | 70 | 0.63 | 32.61 | 1921 | 0 | 49.67 | 2024-10-30 17:06:46.000000 UTC | CPWD MALWANI RECEIVING STATION | 2024-10-30 16:46:41.000000 UTC | Section
1000 | VANDRE | 33 KV | CRITICAL | TATA''S DHARAVI REC-STN | T33DHAOG9H24 | PALI REC-STN | 33236 | 400 | XLPE | 2024-10-29 22:12:00.000000 UTC | 2024-10-29 22:12 | 10 |  | 69 | 2024-10-31 07:54:16.000000 UTC | 210 |  |  |  | NO EXCAVATION ALONG THE ROUTE | 17 |  | Y Phase Faulty at 3000 Meters from PALI REC-STN Fault Pinpointed at on western express highway below new flyover in the garden Total length : 7500 Meters. |  | SYSTEM NORMALIZE | 23 | Straight Joint Faulty |  | Fault Details | 33kV Cable fault | [9 empty] | 2024-10-31 13:44:35.000000 UTC | TATA''S DHARAVI REC-STN | 2024-10-29 23:04:52.000000 UTC | Incommer Line
1000 | VANDRE | 11 KV | MODERATE | JUHU REC-STN | 28483 | JUHU BEACH RESORT | 18713 | 240+300 | PILC+XLPE | 2024-10-01 01:22:38.000000 UTC | 2024-10-01 01:23 | 10 | 1 | 97 | 2024-10-03 07:31:02.000000 UTC | 0 | 0 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 3 | 3 | Y Phase Faulty at 2013 Meters from JUHU REC-STN Fault Pinpointed at ON FOOTPATH NEAR JW MARRIAT HOTEL GATE NO. 1 |  |  | 19 | Transition Joint Faulty |  | Fault Details |  | MONSOON | 0 | 00:00:00 | 0 | 0 | 32.36 | 1784 | 0.25 | 51.97 |  | JUHU REC-STN | 2024-10-01 01:28:55.000000 UTC | Section
3000 |  | 11 KV | MODERATE | MAHARAJA TOWER | 19592 | SUCHIDHAM NO.2 | 28555 | 240+300 | PILC+XLPE | 2024-10-01 16:52:08.000000 UTC | 2024-10-01 16:52 | 10 | 1 | 97 | 2024-10-05 07:59:18.000000 UTC | 260 | 150 | 100 | 1 | NO EXCAVATION ALONG THE ROUTE | 7 | 1 | B Phase Faulty at 240 Meters from MAHARAJA TOWER Fault Pinpointed at arunkumar vaidya marg, nr dream car decor shop Total length : 1700 Meters. |  |  | 19 | Transition Joint Faulty |  | Fault Details |  | MONSOON | 126 | 23:51:00 | 95 | 0.75 | 29.56 | 1883 | 0 | 30.02 |  | DINDOSHI REC-STN | 2024-10-01 17:06:31.000000 UTC | Section
7000 |  | 11 KV | MODERATE | REPUBLIC | 4365 | GULMARG | 29358 | 225+300 | PILC+XLPE | 2024-10-01 04:55:22.000000 UTC | 2024-10-01 04:55 | 10 | 9 | 97 | 2024-10-05 07:42:50.000000 UTC | 115 | 15 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 8 | 2 | B Phase Faulty at 26 Meters from REPUBLIC Fault Pinpointed at INSIDE REPUBLIC PREMISIS Total length : 226 Meters. |  | SYSTEM NORMALIZE | 4 | Fault Bypassed |  | Fault Details |  | MONSOON | 173 | 23:05:00 | 156 | 0.9 | 32.36 | 1784 | 0.25 | 51.97 | 2024-10-02 19:35:47.000000 UTC | CHUNABHATTI REC-STN | 2024-10-01 05:19:56.000000 UTC | Section
1000 |  | 11 KV | CRITICAL | STATE TRANSPORT ROAD NO.2 | 6647 | SAVOY CHAMBER | 34808 | 240+300 | PILC+XLPE | 2024-11-30 12:05:00.000000 UTC | 2024-11-30 12:05 | 11 | 6 | 37 | 2024-12-02 23:20:58.000000 UTC | 147 | 15 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 3 | 8 | Y phase faulty at a distance of 129 meters from State Transport Road No.2 Sub Station Switch Number 6647 . Fault pinpointed UNDER SWD, AT JUNCTION OF DATTATRAY ROAD AND TAGORE NAGAR ROAD JUNCTION, NEAR TO ANURAG BUILDING. Shown to SHARAD. Total length 348 meter. |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | WINTER | 156 | 11:49:00 | 129 | 0.83 | 31.72 | 1429 | 0 | 32.03 | 2024-12-03 01:33:03.000000 UTC | SARASWATI RD. REC-STN | 2024-11-30 15:02:37.000000 UTC | Section
3000 |  | 11 KV | CRITICAL | CHINCHAVLI DAZE | 41680 | CHINCHAVLI CENTRAL NO.2 | 11660 | 300 | XLPE | 2024-11-30 13:33:00.000000 UTC | 2024-11-30 13:33 | 11 | 3 | 37 | 2024-12-02 23:38:48.000000 UTC | 32 | 20 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 8 | Fault Pinpointed at R phase faulty at a distance of 96 meters from Chinchavli Central No.2 Substation Switch Number 11660 . Fault pinpointed CHINCHVALI INTERNAL RD, NEAR VASANT BLDG. Shown to MU. Total length 216 meter. |  |  | 1 | Running Cable Fault |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | WINTER | 49 | 37.5 | 37.5 | 0.77 | 31.72 | 1429 | 0 | 32.03 |  | CHINCHAVLI REC-STN | 2024-11-30 15:02:59.000000 UTC | Section
6000 |  | 11 KV | MODERATE | HCC REC-STN | 31266 | CIPLA | 4448 | 300 | XLPE | 2024-11-29 23:43:00.000000 UTC | 2024-11-29 23:43 | 11 | 1 | 38 | 2024-12-03 23:36:08.000000 UTC | 26 | 26 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 0 | B phase faulty at a distance of 580 meters from Cipla Sub Station Switch Number 4448 . Fault pinpointed NEAR RAJ LEGACY BLDG ON LBS ROAD. Shown to NARSIMA. Total length 1270 meter. |  | SYSTEM NORMALIZE | 4 | Fault Bypassed |  | Fault Details |  | WINTER | 67 | 14:59:00 | 40 | 0.6 | 30.95 | 1481 | 0 | 29.51 | 2024-12-03 23:50:04.000000 UTC | HCC REC-STN | 2024-11-30 02:42:17.000000 UTC | Section
4000 |  | 11 KV | MODERATE | SUNDER DHAM | 29063 | HARI OM APARTMENT | 42081 | 120+150 | PILC+XLPE | 2024-11-30 15:19:00.000000 UTC | 2024-11-30 15:19 | 11 | 9 | 37 | 2024-11-30 23:30:46.000000 UTC | 86 | 30 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 3 | 2 |  |  | SYSTEM NORMALIZE | 22 | Cable Damaged |  | Fault Details |  | WINTER | 113 | 10:40:00 | 75 | 0.66 | 31.72 | 1429 | 0 | 32.03 | 2024-11-30 22:02:32.000000 UTC | SHIMPOLI REC-STN | 2024-11-30 16:07:33.000000 UTC | Section
4000 |  | 11 KV | MODERATE | RAM BAUG | 16398 | SUNDER DHAM | 17848 | 120 | PILC | 2024-11-30 16:39:00.000000 UTC | 2024-11-30 16:39 | 11 | 8 | 37 | 2024-12-01 23:17:06.000000 UTC | 93 | 10 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 2 | 1 |  |  |  | 22 | Cable Damaged |  | Fault Details |  | WINTER | 131 | 15:30:00 | 75 | 0.57 | 31.72 | 1429 | 0 | 32.03 |  | SHIMPOLI REC-STN | 2024-11-30 17:34:59.000000 UTC | Section
1000 |  | 11 KV | CRITICAL | IRLA SOUTH | 9297 | VINAYAK | 32958 | 0.15+185+240+300 | PILC+XLPE | 2024-12-07 10:41:08.000000 UTC | 2024-12-07 10:41 | 12 | 2 | 30 | 2024-12-08 23:01:25.000000 UTC | 100 | 88 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 10 | 2 | Y phase faulty at a distance of 158 meters from VINAYAK Sub Station Switch Number 32958 . Fault pinpointed Fault pinpointed SV ROAD OPP MODERN CERAMICS NEAR ST POLE NO:KBC099077.. Shown to SHARAD. Total length 820 meter. |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details | PRIME AREA | WINTER | 134 | 16:30:00 | 92 | 0.69 | 33.43 | 1645 | 0 | 35.46 | 2024-12-08 22:23:37.000000 UTC | JUHU REC-STN | 2024-12-07 12:27:54.000000 UTC | Section
2000 |  | 11 KV | CRITICAL | SAIFEE MAROL HTC | 40982 | RAHUL | 28587 | 300 | XLPE | 2024-12-08 13:10:00.000000 UTC | 2024-12-08 13:10 | 12 | 2 | 29 |  | 73 | 50 | 0 | 0 | EXCAVATION ALONG THE ROUTE |  | 2 |  |  |  | 22 | Cable Damaged |  | Fault Details | LOAD CURTAILMENT FOR (N-2) SYSTEM | [10 empty] | SAHAR PLAZA REC-STN | 2024-12-08 14:37:10.000000 UTC | Section
4000 |  | 11 KV | CRITICAL | RAJ SARITA | 31051 | BHAKTIDHAM | 14970 | 300 | XLPE | 2024-12-07 14:23:00.000000 UTC | 2024-12-07 14:23 | 12 | 8 | 30 | 2024-12-08 23:46:53.000000 UTC | 66 | 0 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 7 | Fault Pinpointed at B phase faulty at a distance of 50 meters from Raj Sarita Sub Station Switch Number . Fault pinpointed NEAR PILLAR 31091101 OPPOSITE POLE 69/04. Shown to NARESH. Total length 475 meter. |  |  | 22 | Cable Damaged |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | WINTER | 92 | 16:30:00 | 64 | 0.7 | 33.43 | 1645 | 0 | 35.46 |  | GORAI REC-STN | 2024-12-07 15:37:45.000000 UTC | Section
5000 |  | 11 KV | MODERATE | KHARI EAST NO 1 | 6235 | PARASNATH JAIN | 13418 | 150 | XLPE | 2024-12-07 10:50:00.000000 UTC | 2024-12-07 10:50 | 12 | 4 | 30 | 2024-12-11 21:48:38.000000 UTC | 138 | 50 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 5 | 1 |  |  |  | 22 | Cable Damaged |  | Fault Details |  | WINTER | 153 | 11:29:00 | 60 | 0.39 | 33.43 | 1645 | 0 | 35.46 |  | BHAYANDAR REC-STN | 2024-12-07 13:15:34.000000 UTC | Section
4000 |  | 11 KV | MODERATE | GURU KRIPA | 5501 | BORIVALI EAST NO 4 | 19849 | 240 | PILC | 2024-12-07 11:02:00.000000 UTC | 2024-12-07 11:02 | 12 | 9 | 30 | 2024-12-08 23:47:20.000000 UTC | 119 | 20 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 2 | Fault Pinpointed at Y phase faulty at a distance of 120 meters from Guru Kripa (Plt) Sub Station Switch Number 5501 . Fault pinpointed CHINCHPADA ROAD NEAR ABHYUDAYA COPERATIVE BANK LIMITED. Shown to NARESH. Total length 422 meter. |  |  | 4 | Fault Bypassed |  | Fault Details |  | WINTER | 134 | 18:21:00 | 78 | 0.58 | 33.43 | 1645 | 0 | 35.46 |  | DEVIDAS LANE REC-STN | 2024-12-07 13:13:09.000000 UTC | Section
1000 |  | 11 KV | CRITICAL | BANDRA TALKIES | 18896 | BANDRA NORTH | 2890 | 300 | XLPE | 2024-12-07 12:27:00.000000 UTC | 2024-12-07 12:27 | 12 | 2 | 30 | 2024-12-07 16:33:33.000000 UTC | 60 | 20 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 17 | 3 |  |  | SYSTEM NORMALIZE | 22 | Cable Damaged |  | Fault Details | SUBSTATIONS ARE AFFECTED | WINTER | 141 | 12:10:00 | 110 | 0.78 | 33.43 | 1645 | 0 | 35.46 | 2024-12-07 19:50:11.000000 UTC | BANDRA REC-STN | 2024-12-07 14:05:31.000000 UTC | Section
6000 |  | 11 KV | CRITICAL | GANGES INK | 15992 | INDRAPRASTHA 1 | 15809 | 185+240 | PILC+XLPE | 2024-09-23 18:37:00.000000 UTC | 2024-09-23 18:37 | 9 | 6 | 105 | 2024-09-26 00:28:37.000000 UTC | 123 | 35 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE |  | 6 | R Phase Faulty at 15 Meters from INDRAPRASTHA 1 Fault Pinpointed at IN THE COMPOUND OF INDRAPRASTHA CSS |  |  | 1 | Running Cable Fault |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | MONSOON | 139 | 10:11:00 | 90 | 0.65 | 30.8 | 1882 | 37.5 | 46.7 |  | HCC REC-STN | 2024-09-23 20:41:27.000000 UTC | Section
6000 | POWAI | 22 KV | CRITICAL | TILAK NAGAR REC-STN | 33054 | VIKHROLI REC-STN | 33012 | 300 | XLPE | 2024-09-23 13:57:00.000000 UTC | 2024-09-23 13:57 | 9 |  | 105 | 2024-09-27 04:25:29.000000 UTC | 86 |  |  |  | NO EXCAVATION ALONG THE ROUTE | 3 |  | R Phase Faulty at 4012 Meters from TILAK NAGAR REC-STN Fault Pinpointed at Fault pinpointed FPP ON AGLR NEAR GHATKOPAR BUS DEPO 20M FROM NALA. Shown to NARSIMHA. Total length 6000 meter. |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details | 22kV Cable fault | MONSOON | 113 | 94.5 | 94.5 | 0.84 | 30.88 | 1882 | 35.5 | 46.66 | 2024-09-26 19:52:08.000000 UTC | TATA''S VIKHROLI REC-STN | 2024-09-25 09:41:36.000000 UTC | Incommer Line
2000 |  | 11 KV | MODERATE | MAHANANDA REC-STN | 26032 | MAJAS WEST | 13341 | 240+300 | PILC+XLPE | 2024-11-10 04:15:14.000000 UTC | 2024-11-10 04:15 | 11 | 1 | 57 | 2024-11-13 18:53:54.000000 UTC | 11 | 11 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 29 | 0 | Y phase faulty at a distance of 1202 meters from Mahananda R/S Switch Number 26032 . Fault pinpointed OPP BALASAHED THACKERY TRAUMA CENTRE INSIDE METRO EXCAVATION. . Shown to janardhan. Total length 1710 meter. |  | SYSTEM NORMALIZE | 4 | Fault Bypassed |  | Fault Details |  | WINTER | 45 | 12:14:00 | 25 | 0.56 | 34.03 | 1491 | 0 | 34.3 | 2024-11-11 22:22:03.000000 UTC | MAHANANDA REC-STN | 2024-11-10 04:53:31.000000 UTC | Section
3000 |  | 11 KV | CRITICAL | GORASWADI ROAD NO.2 | 37911 | ADARSH VIHAR | 11856 | 300 | XLPE | 2024-11-10 12:58:00.000000 UTC | 2024-11-10 12:58 | 11 | 2 | 57 | 2024-11-10 18:46:38.000000 UTC | 100 | 90 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 2 | 1 | B Phase Faulty at 239 Meters from ADARSH VIHAR Fault Pinpointed at FP ON SHAKTI NGR RD NEAR SHAKTI NGR RD Total length : 246 Meters. |  |  | 22 | Cable Damaged |  | Fault Details | LOAD CURTAILMENT FOR (N-2) SYSTEM | WINTER | 113 | 16:30:00 | 88 | 0.78 | 29.37 | 1491 | 0 | 34.3 |  | MALAD REC-STN | 2024-11-10 14:39:44.000000 UTC | Section
2000 |  | 11 KV | MODERATE | EIH UNIT OBEROI FLIGHTS | 41199 | MAROL NAKA NO.2 | 15550 | 240+300 | PILC+XLPE | 2024-11-16 22:36:00.000000 UTC | 2024-11-16 22:36 | 11 | 8 | 51 | 2024-11-20 23:52:13.000000 UTC | 53 | 10 | 10 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 4 | Fault Pinpointed at R&B PHASE FAULTY AT THE DISTANCE OF 374 MTRS FROM MAROL NAKKA NO.1 CSS, FAULT PINPOINTED NEAR MAROL NAKA NO.2 CSS, SHOWN TO GANESH, TOTAL LENGTH:2075 MTR |  |  | 22 | Cable Damaged |  | Fault Details |  | WINTER | 78 | 11:02:00 | 61 | 0.78 | 33.98 | 1701 | 0 | 41.01 |  | J. B. NAGAR RECEIVING STATION | 2024-11-16 23:58:40.000000 UTC | Section
1000 |  | 11 KV | MODERATE | V MALL | 36346 | SANTACRUZ NORTH NO.1 | 4328 | 300 | XLPE | 2024-11-16 00:08:00.000000 UTC | 2024-11-16 00:08 | 11 | 5 | 51 | 2024-11-19 23:08:39.000000 UTC | 67 | 6 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 2 | B Phase Faulty at 140 Meters from SANTACRUZ NORTH NO.1 Fault Pinpointed at OPPOSITE TO TALERIKA SHOP ON SV ROAD. SHOWN TO SAWANT. |  |  | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 134 | 15:30:00 | 81 | 0.6 | 33.98 | 1701 | 0 | 41.01 |  | SHRADDHANAND ROAD REC-STN | 2024-11-16 00:46:33.000000 UTC | Section
4000 |  | 11 KV | MODERATE | KANDIVLI REC-STN | 16781 | AKURLI ROAD NO.1 | 13895 | 300 | XLPE | 2024-11-16 20:50:00.000000 UTC | 2024-11-16 20:50 | 11 | 1 | 51 | 2024-11-23 23:32:49.000000 UTC | 77 | 0 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 10 | 2 | RB Phase Faulty at 890 Meters from KANDIVLI REC-STN Fault Pinpointed at AKURLI ROAD NEAR STREET LIGHT POLW WDG00034,OPPO ESIS HOSPITAL Total length : 970 Meters. |  |  | 4 | Fault Bypassed |  | Fault Details |  | WINTER | 108 | 75 | 75 | 0.69 | 33.98 | 1701 | 0 | 41.01 |  | KANDIVLI REC-STN | 2024-11-17 07:46:13.000000 UTC | Section
1000 |  | 11 KV | MODERATE | MOTILAL NEHRU NAGAR NO 2 | 29037 | PINNACLE CORP. PLAZA | 32732 | 300 | XLPE | 2024-11-16 14:22:00.000000 UTC | 2024-11-16 14:22 | 11 | 2 | 51 | 2024-11-17 23:10:40.000000 UTC | 95 | 80 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 2 | 2 | RYB Phase Faulty at 250 Meters from MOTILAL NEHRU NAGAR NO 2 Fault Pinpointed at Fault pinpointed OPPOSITE TO SWAGAT HOTEL GATE ON MOTILAL NGR ROAD Total length : 400 Meters. |  |  | 4 | Fault Bypassed |  | Fault Details |  | WINTER | 128 | 14:47:00 | 96 | 0.68 | 33.98 | 1701 | 0 | 41.01 |  | MMRDA REC-STN | 2024-11-16 14:53:40.000000 UTC | Section
4000 | BORIWALI | 33 KV | CRITICAL | 220kV GHODBUNDER REC-STN | 220GHO61 | DAHISAR REC-STN | 33059 | 400 | XLPE | 2024-09-16 22:06:00.000000 UTC | 2024-09-16 22:06 | 9 |  | 112 | 2024-09-21 23:52:42.000000 UTC | 104 |  |  |  | NO EXCAVATION ALONG THE ROUTE | 23 |  | Fault Pinpointed at RB PHASE FAULTY AT A DISTANCE OF 1959 MTRS FROM GHD R/S FPP OPPO MAKE TOWN TOWER NEAR POLE XKM 002/111 TOTAL LENGTH 6531 MTRS SHOWN TO MAHESH |  |  | 23 | Straight Joint Faulty |  | Fault Details | 33kV Cable fault | [10 empty] | 220kV GHODBUNDER REC-STN | 2024-09-16 22:47:43.000000 UTC | Incommer Line
6000 |  | 11 KV | CRITICAL | SWAN MILL REC-STN | 34557 | KURLA 3 | 35196 | 300 | XLPE | 2024-09-16 01:20:00.000000 UTC | 2024-09-16 01:20 | 9 | 1 | 112 | 2024-09-26 23:38:51.000000 UTC | 140 | 140 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 8 | 0 | B Phase Faulty at 120 Meters from KURLA NO.3 CSS Fault Pinpointed at ON NEW MILL ROAD BRIDGE NEAR LT PILLAR NUMBER 11111505 |  |  | 1 | Running Cable Fault |  | Fault Details | LOAD CURTAILMENT FOR (N-2) SYSTEM | MONSOON | 141 | 19:26:00 | 118 | 0.84 | 32.44 | 1734 | 0 | 43.78 |  | SWAN MILL REC-STN | 2024-09-16 01:34:00.000000 UTC | Section
3000 |  | 11 KV | MODERATE | ANAND ROAD | 12025 | MALAD SHOPPING CENTRE | 10086 | 120 | PILC | 2024-11-14 15:54:00.000000 UTC | 2024-11-14 15:54 | 11 | 8 | 53 | 2024-11-17 23:59:58.000000 UTC | 135 | 30 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 2 | R Phase Faulty at 85 Meters from LINGYAANAND ROAD Fault Pinpointed at FP NEAR MALAD SHOPING CENTRE CSS Total length : 101 Meters. |  |  | 4 | Fault Bypassed |  | Fault Details |  | WINTER | 138 | 15:30:00 | 87 | 0.63 | 35.39 | 1705 | 0 | 37.47 |  | CHINCHAVLI REC-STN | 2024-11-14 17:54:24.000000 UTC | Section
7000 |  | 11 KV | CRITICAL | GOLF SCAPEE | 28524 | MASKA CHAWL | 29808 | 225+240+300 | PILC+XLPE | 2024-11-14 21:27:16.000000 UTC | 2024-11-14 21:27 | 11 | 13 | 53 | 2024-11-17 23:41:13.000000 UTC | 133 | 10 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 1 | 5 | Y Phase Faulty at 286 Meters from GOLF SCAPEE Fault Pinpointed at ON SION TROBAY Road , infroft of sai signature undervonstructioon buuilding.. Total length : 323 Meters. |  |  | 1 | Running Cable Fault |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | WINTER | 154 | 14:12:00 | 100 | 0.65 | 35.39 | 1705 | 0 | 37.47 |  | MHADA SAHAKAR NGR REC-STN | 2024-11-14 22:21:44.000000 UTC | Section
1000 |  | 11 KV | CRITICAL | DANDA VILLAGE NO.2 | 14672 | DANDA VILLAGE NO.4 | 42296 | 120 | PILC | 2024-11-14 14:35:00.000000 UTC | 2024-11-14 14:35 | 11 | 10 | 53 | 2024-11-15 17:07:09.000000 UTC | 111 | 0 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 3 | 5 | B Phase Faulty at 272 Meters from DANDA VILLAGE NO.4 Fault Pinpointed at ON KHAR DANDA ROAD NEAR RIZVI SPRING FIELD HIGH SCHOOL |  |  | 4 | Fault Bypassed |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | WINTER | 178 | 11:59:00 | 162 | 0.91 | 35.39 | 1705 | 0 | 37.47 |  | KHAR REC-STN | 2024-11-14 14:52:19.000000 UTC | Section
1000 |  | 11 KV | CRITICAL | RELIANCE IND. OFF SITE (T) | 43035 | MCA | 30648 | 300 | XLPE | 2024-11-14 15:11:00.000000 UTC | 2024-11-14 15:11 | 11 | 3 | 53 | 2024-11-14 17:10:45.000000 UTC | 35 | 0 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 3 | B Phase Faulty at 152 Meters from RELIANCE IND OFF SITE CSS Fault Pinpointed at FPP NEAR WE WORK BLDG |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details | PRIME AREA | WINTER | 40 | 10:01:00 | 35 | 0.88 | 35.39 | 1705 | 0 | 37.47 | 2024-11-14 23:48:15.000000 UTC | GODREJ BKC REC-STN | 2024-11-14 15:22:31.000000 UTC | Section
1000 |  | 11 KV | MODERATE | ACME MALL | 35197 | V MALL | 36348 | 300 | XLPE | 2024-11-14 10:49:00.000000 UTC | 2024-11-14 10:49 | 11 | 4 | 53 | 2024-11-15 12:02:32.000000 UTC | 101 | 20 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 2 | 2 |  |  | SYSTEM NORMALIZE | 22 | Cable Damaged |  | Fault Details |  | WINTER | 134 | 17:15:00 | 90 | 0.67 | 35.39 | 1705 | 0 | 37.47 | 2024-11-15 07:37:23.000000 UTC | SHRADDHANAND ROAD REC-STN | 2024-11-14 11:37:53.000000 UTC | Section
6000 | POWAI | 22 KV | CRITICAL | 220 kV AAREY EHV STATION | 220AAR41 | NAHAR SHAKTI REC-STN | 33207 | 400 | XLPE | 2024-11-14 04:57:00.000000 UTC | 2024-11-14 04:57 | 11 |  | 53 | 2024-11-18 23:47:01.000000 UTC | 105 |  |  |  | NO EXCAVATION ALONG THE ROUTE | 2 |  | R Phase Faulty at 620 Meters from 220 kV AAREY EHV STATION Fault Pinpointed at ON JVLR ROAD OPPO MUM METRO RAIL OFC NEAR HUT.. Shown to ANJYA Total length : 4112 Meters. |  |  | 23 | Straight Joint Faulty |  | Fault Details | 33kV Cable fault | [10 empty] | NAHAR SHAKTI REC-STN | 2024-11-14 08:46:37.000000 UTC | Incommer Line
6000 |  | 11 KV |  | CHANDIVLI SRA REC-STN | 30998 |  |  |  |  | 2024-09-27 17:56:00.000000 UTC | 2024-09-27 17:56 | 9 |  | 101 | [10 empty] | SYSTEM NORMALIZE | 5 | Termination Faulty |  | Fault Details | [10 empty] | 2024-09-28 13:20:52.000000 UTC | CHANDIVLI SRA REC-STN | 2024-09-27 18:12:58.000000 UTC | Breaker/Switch
4000 |  | 11 KV | MODERATE | MHATRE ROAD NO 1 | 15435 | MANDPESHWAR NORTH NO 1 | 9182 | 300 | XLPE | 2024-09-27 15:07:00.000000 UTC | 2024-09-27 15:07 | 9 | 6 | 101 | 2024-09-30 06:34:07.000000 UTC | 50 | 0 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 1 | 0 | Fault Pinpointed at B PHASE FAULTY AT A DISTANCE OF 120 MTRS FROM MNDPESHWAR NORHT S/S FPP LAXMAN MHATRE NEAR TWO WAY 30100906 SHOWN TO NARESH TOTAL LENGTH 384 MTRS |  |  | 1 | Running Cable Fault |  | Fault Details |  | MONSOON | 80 | 23:03:00 | 50 | 0.63 | 26.97 | 1717 | 84 | 31.29 |  | DAHISAR WEST REC-STN | 2024-09-27 16:05:45.000000 UTC | Section
7000 |  | 11 KV | MODERATE | TROMBAY TOWNSHIP CLY | 2927 | ASHA PICTURE | 14001 | 225+300+400 | PILC+XLPE | 2024-10-02 05:01:00.000000 UTC | 2024-10-02 05:01 | 10 | 4 | 96 | 2024-10-05 23:44:27.000000 UTC | 5 | 0 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 17 | 0 | Y Phase Faulty at 828 Meters from ASHA PIUCTURE Fault Pinpointed at Fault pinpointed BEHIND CHRISTIAN FELLOWSHIP CHURCH, 2 METERS FROM TREE. Total length 1029 meter. Total length : 1029 Meters. |  |  | 1 | Running Cable Fault |  | Fault Details |  | MONSOON | 5 | 18:37:00 | 3 | 0.6 | 29.56 | 1883 | 0 | 30.02 |  | ACROPOLIS REC-STN | 2024-10-02 06:42:47.000000 UTC | Section
6000 |  | 11 KV | MODERATE | KARANI LANE | 7780 | GHATKOPAR CENTRAL 2 | 9532 | 0.6+70+120 | PILC | 2024-10-02 05:18:00.000000 UTC | 2024-10-02 05:18 | 10 | 4 | 96 | 2024-10-05 23:34:01.000000 UTC | 54 | 14 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 2 | 0 | Faulty at 280 Meters from KARANI LANE Fault Pinpointed at TNEAR TRAFFIC SIGNAL,BELOW SIGN BOARD OF BMC AND NEAR STREET LIGHT POLE NO - NGW/001/041 Total length : 363 Meters. |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details |  | MONSOON | 78 | 19:39:00 | 66 | 0.85 | 29.56 | 1883 | 0 | 30.02 | 2024-10-05 17:16:14.000000 UTC | VIKHROLI REC-STN | 2024-10-02 06:29:59.000000 UTC | Section
1000 |  | 11 KV | CRITICAL | SHIVAM CENTRIUM | 37618 | OM SAI GANGA | 35269 | 240+300 | PILC+XLPE | 2024-10-02 12:38:00.000000 UTC | 2024-10-02 12:38 | 10 | 2 | 96 | 2024-10-03 15:10:37.000000 UTC | 75 | 62 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 1 | 4 | RYB Phase Faulty at 157 Meters from SHIVAM CENTRIUM Fault Pinpointed at Fault pinpointed on Shara Road opposite vimal intertrade. Shown to SAWANT. Total length 600 meter. Total length : 600 Meters. |  |  | 19 | Transition Joint Faulty |  | Fault Details | LOAD CURTAILMENT FOR (N-2) SYSTEM | MONSOON | 85 | 23:00:00 | 65 | 0.76 | 32.36 | 1787 | 0 | 51.97 |  | SAMBHAJI NAGAR REC-STN | 2024-10-02 14:21:58.000000 UTC | Section
6000 | POWAI | 11 KV | CRITICAL | CHANDIVALI GODREJ URBAN PARK | 42632 | R.K.POLYMER | 15627 | 120+300 | PILC+XLPE | 2024-10-02 11:54:00.000000 UTC | 2024-10-02 11:54 | 10 | 3 | 96 | 2024-10-03 01:00:13.000000 UTC | 50 | 10 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE |  | 2 | R Phase Faulty at 217 Meters from RK POLYMER Fault Pinpointed at FPP ON VIJAY FIRE RD OPPOSITE MCGM OFFICE SHOWN TO UPPAL Total length : 1178 Meters. |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details |  | MONSOON | 54 | 25 | 25 | 0.46 | 32 | 1787 | 0 | 51 | 2024-10-03 21:07:46.000000 UTC | CHANDIVLI SRA REC-STN | 2024-10-02 16:00:01.000000 UTC | Section
3000 |  | 11 KV |  | AAREY GUEST HOUSE KIOSK NO.2 | 17175 |  |  |  |  | 2024-09-25 14:09:04.000000 UTC | 2024-09-25 14:09 | 9 |  | 103 | [10 empty] | SYSTEM NORMALIZE | 57 | HT Consumer Network Problem |  | Fault Details | [10 empty] | 2024-09-26 01:39:31.000000 UTC | AAREY GUEST HOUSE KIOSK NO.2 | 2024-09-26 01:38:22.000000 UTC | HT Consumer
3000 |  | 11 KV |  | AKURLI ROAD NORTH NO.2 | 16309 |  |  |  |  | 2024-09-25 18:51:00.000000 UTC | 2024-09-25 18:51 | 9 |  | 103 | [10 empty] | SYSTEM NORMALIZE | 57 | HT Consumer Network Problem |  | Fault Details | [10 empty] | 2024-09-26 00:23:24.000000 UTC | AKURLI ROAD NORTH NO.2 | 2024-09-26 00:19:17.000000 UTC | HT Consumer
5000 |  | 11 KV | CRITICAL | SHALOM RESIDENCY | 31961 | SALASAR AANGAN | 38625 | 300 | XLPE | 2024-09-25 17:56:00.000000 UTC | 2024-09-25 17:56 | 9 | 11 | 103 | 2024-09-28 21:55:43.000000 UTC | 108 | 40 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 9 | Fault Pinpointed at RY PHASE FAULTY AT A DISTANCE OF 100 METERS F...ROM SHALOM RESIDENCY SUBSTATION SWITCH NUMBER 31961 . FAULT PINPOINTED NEAR POLE NO. XUA083/001, OPP. SAI SHRUSHA HOTEL. SHOWN TO LINGYA. TOTAL LENGTH 988 METER. |  |  | 4 | Fault Bypassed |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | MONSOON | 156 | 111 | 111 | 0.71 | 31.18 | 1816 | 0 | 30.09 |  | GHODBUNDER REC-STN | 2024-09-25 20:44:38.000000 UTC | Section
6000 |  | 11 KV | CRITICAL | GANGES INK | 15992 | INDRAPRASTHA 1 | 15809 | 185+240+300 | PILC+XLPE | 2024-09-25 13:31:00.000000 UTC | 2024-09-25 13:31 | 9 | 4 | 103 | 2024-09-28 16:27:50.000000 UTC | 176 | 70 | 50 | 1 | NO EXCAVATION ALONG THE ROUTE | 6 | 6 | YB Phase Faulty at 249 Meters from GANGES INK Fault Pinpointed at ON LBS ROAD NEAR NAND ROVER SERVICE CENTER GATE, Total length : 399 Meters. |  | SYSTEM NORMALIZE | 19 | Transition Joint Faulty |  | Fault Details | SUBSTATIONS ARE AFFECTED | MONSOON | 115 | 12:16:00 | 90 | 0.78 | 31.18 | 1816 | 178 | 48.05 | 2024-09-26 20:31:57.000000 UTC | HCC REC-STN | 2024-09-25 15:08:11.000000 UTC | Section
5000 |  | 11 KV | CRITICAL | SHIVDARSHAN BUILDING | 34772 | EDEN ROSE | 17132 | 240+300 | PILC+XLPE | 2024-09-25 17:38:00.000000 UTC | 2024-09-25 17:38 | 9 | 3 | 103 | 2024-09-30 21:54:46.000000 UTC | 109 | 80 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 4 | 9 |  |  |  | 22 | Cable Damaged |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | MONSOON | 140 | 99 | 99 | 0.71 | 31.18 | 1816 | 0 | 30.9 |  | SADGURU REC-STN | 2024-09-25 20:39:37.000000 UTC | Section
5000 |  | 11 KV |  | RAIPADA | 4135 |  |  |  |  | 2024-09-28 03:42:00.000000 UTC | 2024-09-28 03:42 | 9 |  | 100 | [10 empty] | SYSTEM NORMALIZE | 12 | Busbar Flashover |  | Fault Details | [10 empty] | 2024-10-02 11:06:21.000000 UTC | BHAYANDAR WEST REC-STN | 2024-09-28 06:43:58.000000 UTC | Busbar and Circuit
4000 |  | 11 KV | MODERATE | K.I.E. REC-STN | 35884 | ASSOCIATED CAPSULE | 13154 | 240+300 | PILC+XLPE | 2024-12-05 14:20:00.000000 UTC | 2024-12-05 14:20 | 12 | 1 | 32 | 2024-12-07 23:00:57.000000 UTC | 14 | 14 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 4 | 1 | R phase faulty at a distance of 460 meters from Kie R/S Switch Number 26308 . Fault pinpointed NEAR PLOT NO 28 A/B LIBA ENTERPRISES ON CHARKOP SERIVCE ROAD. Shown to FRANCIS. Total length 756 meter. |  |  | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 18 | 11:27:00 | 10 | 0.56 | 34.94 | 1803 | 0 | 44.25 |  | K.I.E. REC-STN | 2024-12-05 14:36:49.000000 UTC | Section
3000 |  | 11 KV | MODERATE | KALPATARU RADIANCE | 39272 | GOREGAON REC-STN | 1534 | 240+300 | PILC+XLPE | 2024-12-05 12:01:31.000000 UTC | 2024-12-05 12:02 | 12 | 4 | 32 | 2024-12-06 23:21:53.000000 UTC | 33 | 0 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 7 | 3 | Y phase faulty at a distance of 549 meters from Kalpataru Radiance Substation Switch Number 39272 . Fault pinpointed sidhharth ngr road no.10 oppo. maharashtra medical.. Shown to reddy. Total length 781 meter. |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 39 | 18:34:00 | 24 | 0.62 | 34.94 | 1803 | 0 | 44.25 | 2024-12-06 21:44:09.000000 UTC | OSHIWARA RECEIVING STATION | 2024-12-05 12:04:42.000000 UTC | Section
2000 |  | 11 KV | CRITICAL | APANA GHAR NO.1 | 9312 | VERSOVA MHADA NO.3 | 32151 | 240+300 | PILC+XLPE | 2024-12-06 16:26:00.000000 UTC | 2024-12-06 16:26 | 12 | 5 | 31 | 2024-12-09 00:58:35.000000 UTC | 130 | 41 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 4 |  | CABLE DAMAGED INFRONT OF INDRA LOK BUILDING GATE, NEAR LOKHANDWALA CIRCLE, ON LOKHANWALA COMPLEX ROAD, BY MCGM (METRO WORK) |  | 22 | Cable Damaged |  | Fault Details | LOAD CURTAILMENT FOR (N-2) SYSTEM | WINTER | 135 | 11:07:00 | 88 | 0.65 | 34.28 | 1841 | 0 | 44.77 |  | AMBIVLI REC-STN | 2024-12-06 18:09:48.000000 UTC | Section
1000 | VANDRE | 33 KV | CRITICAL | 220kV SAKI REC-STN | 220SAK32 | KALINA REC-STN | 33056 | 400 |  | 2024-12-05 20:41:00.000000 UTC | 2024-12-05 20:41 | 12 |  | 32 | 2024-12-07 07:57:03.000000 UTC | 135 |  |  |  | NO EXCAVATION ALONG THE ROUTE | 7 |  | B Phase Faulty at 1800 Meters from KALINA REC-STN Fault Pinpointed at ON LBS ROAD OPPOSITE PETROL PUMP NEAR POLE NO. LJB 099/009 |  |  | 23 | Straight Joint Faulty |  | Fault Details | 33kV Cable fault | [10 empty] | 220kV SAKI REC-STN | 2024-12-05 21:18:14.000000 UTC | Incommer Line
2000 |  | 11 KV | CRITICAL | MATHURIA APARTMENT | 12045 | GUNDAVLI NO.2 | 5319 | 120 | PILC | 2024-12-05 20:10:00.000000 UTC | 2024-12-05 20:10 | 12 | 6 | 32 | 2024-12-07 23:22:05.000000 UTC | 153 | 70 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 2 | 4 | RYB Phase Faulty at 214 Meters from GUNDAVLI NO.2 Fault Pinpointed at MADHURIYA APPT PRIVATE PRIMISES Total length : 295 Meters. |  |  | 19 | Transition Joint Faulty |  | Fault Details | LOAD CURTAILMENT FOR (N-2) SYSTEM | WINTER | 176 | 15:30:00 | 127 | 0.72 | 34.94 | 1803 | 0 | 44.25 |  | SAMBHAJI NAGAR REC-STN | 2024-12-05 21:20:32.000000 UTC | Section
3000 |  | 11 KV | CRITICAL | ERANGLE REC-STN | 42303 | SUNRISE INFOTECH | 40529 | 300+400 | XLPE | 2024-11-26 12:27:26.000000 UTC | 2024-11-26 12:27 | 11 | 1 | 41 | 2024-11-26 12:53:10.000000 UTC | 55 | 55 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 5 | R Phase Faulty at 98 Meters from SUNRISE INFOTECH Fault Pinpointed at IN FRONT OF GOLDEN NEAST LODGE Total length : 837 Meters. |  |  | 1 | Running Cable Fault |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | WINTER | 130 | 90 | 90 | 0.69 | 32.12 | 1528 | 0 | 30.63 |  | ERANGLE REC-STN | 2024-11-26 12:44:02.000000 UTC | Section
3000 |  | 11 KV | MODERATE | TEEN DONGRI HILL | 13342 | MITHAGAR ROAD NO.2 | 2604 | 300 | XLPE | 2024-11-26 10:23:00.000000 UTC | 2024-11-26 10:23 | 11 | 10 | 41 | 2024-11-28 12:55:19.000000 UTC | 95 | 20 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 4 |  |  | SYSTEM NORMALIZE | 22 | Cable Damaged |  | Fault Details |  | WINTER | 120 | 19:30:00 | 100 | 0.83 | 32.12 | 1528 | 0 | 30.63 | 2024-11-27 17:02:35.000000 UTC | GOREGAON REC-STN | 2024-11-26 11:47:33.000000 UTC | Section
6000 |  | 11 KV | MODERATE | VIKHROLI HILL 1 | 12088 | MAHAJAN SILK MILLS | 5911 | 185+240 | XLPE | 2024-11-26 10:31:00.000000 UTC | 2024-11-26 10:31 | 11 | 10 | 41 | 2024-11-28 01:49:31.000000 UTC | 37 | 0 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 6 | 0 | B phase faulty at a distance of 221 meters from Vikhroli Hill 1 Sub Station Switch Number 12088 . Fault pinpointed NEAR AASHA USHA COMPANY BUS STOP, ON LBS RD . Shown to SHINU . Total length 370 meter. |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 60 | 20:20:00 | 47 | 0.78 | 30.63 | 1528 | 0 | 32.12 | 2024-11-28 18:09:12.000000 UTC | RUNWAL REC-STN | 2024-11-26 12:03:26.000000 UTC | Section
3000 |  | 11 KV |  | AKURLI ROAD NORTH NO.2 | 16309 |  |  |  |  | 2024-09-29 08:15:33.000000 UTC | 2024-09-29 08:16 | 9 |  | 99 | [10 empty] | SYSTEM NORMALIZE | 57 | HT Consumer Network Problem |  | Fault Details | [10 empty] | 2024-09-29 14:48:32.000000 UTC | AKURLI ROAD NORTH NO.2 | 2024-09-29 14:47:15.000000 UTC | HT Consumer
3000 |  | 11 KV | MODERATE | AAREY CROSS ROAD NO. 2 | 7648 | ACCORD CLASSIC | 37861 | 120+300 | PILC+XLPE | 2024-09-29 06:30:00.000000 UTC | 2024-09-29 06:30 | 9 | 10 | 99 | 2024-10-02 07:28:18.000000 UTC | 52 | 0 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 1 | 2 | RY Phase Faulty at 345 Meters from AAREY CROSS ROAD NO. 2 Fault Pinpointed at NEAR AAREY SUBWAY , OPPSITE HARI OM MEDICAL Total length : 843 Meters. |  |  | 19 | Transition Joint Faulty |  | Fault Details |  | MONSOON | 130 | 89 | 89 | 0.68 | 27.41 | 1637 | 0 | 32.76 |  | GOREGAON REC-STN | 2024-09-29 07:14:07.000000 UTC | Section
2000 |  | 11 KV | CRITICAL | DEEP TOWER | 18982 | M H A D A NO.1 | 12889 | 300 | XLPE | 2024-09-29 08:43:00.000000 UTC | 2024-09-29 08:43 | 9 | 2 | 99 | 2024-10-02 23:02:20.000000 UTC | 84 | 50 | 50 | 0 | NO EXCAVATION ALONG THE ROUTE | 4 | 0 | RYB phase faulty at a distance of 430 meters from Deep Tower Substation Switch Number 18982 . Fault pinpointed ON BHAHU TATOBA TORASKAR MARG, OPP. BUILDING NO.19, NEAR MAHESHWARI HALL.. Shown to JANARDHAN . Total length 770 meter. |  |  | 1 | Running Cable Fault |  | Fault Details | LOAD CURTAILMENT FOR (N-2) SYSTEM | MONSOON | 148 | 15:21:00 | 113 | 0.76 | 31.8 | 1453 | 2.5 | 43.31 |  | VERSOVA RECEIVING STATION | 2024-09-29 10:13:01.000000 UTC | Section
7000 |  | 11 KV | CRITICAL | RAJAWADI 1 | 31611 | SOMAYA COMPUTER | 10175 | 120 | PILC | 2024-11-28 14:34:48.000000 UTC | 2024-11-28 14:35 | 11 | 6 | 39 | 2024-11-30 23:08:13.000000 UTC | 92 | 16 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 5 | 5 | B Phase Faulty at 84 Meters from SOMAIYYA COMPUTER Fault Pinpointed at FPP AT RAJAWADI RD NO.7, INFRONT OF SHREENATH KRUPA BLDG Total length : 501 Meters. |  |  | 1 | Running Cable Fault |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | WINTER | 101 | 11:27:00 | 80 | 0.79 | 31.42 | 1501 | 0 | 30.28 |  | HINGWALA LANE REC-STN | 2024-11-28 15:27:57.000000 UTC | Section
3000 |  | 11 KV | MODERATE | BANGUR NAGAR NO.1 | 18149 | VASUPUJYA | 34005 | 300+120 | PILC+XLPE | 2024-11-28 19:25:00.000000 UTC | 2024-11-28 19:25 | 11 | 5 | 39 | 2024-11-29 22:26:55.000000 UTC | 85 | 0 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 2 | 4 |  |  |  | 22 | Cable Damaged |  | Fault Details |  | WINTER | 82 | 16:03:00 | 74.5 | 0.91 | 31.42 | 1501 | 0 | 30.28 |  | MIND SPACE REC-STN | 2024-11-28 20:28:04.000000 UTC | Section
5000 |  | 11 KV | CRITICAL | UTTAN KIOSK | 7181 | SHEREY LANE | 15168 | 120+150+300 | PILC+XLPE | 2024-10-31 16:25:00.000000 UTC | 2024-10-31 16:25 | 10 | 11 | 67 | 2024-11-02 19:55:41.000000 UTC | 155 | 30 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 6 | 5 | Fault Pinpointed at R-PH FAULTY AT DIST OF 873M FROM UTTAN KIOSK S/S, PP OPP. COMMON TOILET AND DOG HOSPITAL, SHERLEY LANE ROAD, SHOWN TO SHANKAR, TOTAL SECTION LENGTH 1260M, EA |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | MONSOON | 160 | 120 | 120 | 0.75 |  |  | 0 |  | 2024-11-06 18:34:33.000000 UTC | BHAYANDAR WEST REC-STN | 2024-10-31 17:40:23.000000 UTC | Section
7000 |  | 22 KV | CRITICAL | TATA''S CHEMBUR REC-STN | T33CHMBOG03 | CHEMBUR REC-STN | 1151 | 0.3+300 |  | 2024-10-31 04:21:00.000000 UTC | 2024-10-31 04:21 | 10 |  | 67 | 2024-11-04 07:43:12.000000 UTC | 51 |  |  |  | NO EXCAVATION ALONG THE ROUTE | 19 |  | Fault Pinpointed at Y phase faulty at a distance of 2900 meters from Chembur R/S Switch Number . Fault pinpointed DULIP SINGH MARG OPPOSITE R K ADMIN BUILDING 10 MTRS FROM NALA. Shown to MILIND. Total length 3310 meter. |  | SYSTEM NORMALIZE | 19 | Transition Joint Faulty |  | Fault Details | 22kV Cable fault | [9 empty] | 2024-11-04 14:41:11.000000 UTC | TATA''S CHEMBUR REC-STN | 2024-10-31 05:05:43.000000 UTC | Incommer Line
6000 |  | 11 KV | MODERATE | CHANDIVALI | 7940 | ADI SHANKARACHARYA MARG 1 | 7443 | 300 | XLPE | 2024-11-09 15:35:20.000000 UTC | 2024-11-09 15:35 | 11 | 5 | 58 | 2024-11-11 23:17:27.000000 UTC | 152 | 0 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 9 | 0 | B Phase Faulty at 150 Meters from CHANDIVALI Fault Pinpointed at NEAR BUDDH VIHAR Total length : 575 Meters. |  |  | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 168 | 11:02:00 | 133 | 0.79 | 34.14 | 1647 | 0 | 34.47 |  | NAHAR SHAKTI REC-STN | 2024-11-09 16:32:15.000000 UTC | Section
3000 |  | 11 KV | MODERATE | FLEMINGO APARTMENT | 31529 | MAN NIKETAN | 29703 | 240+300 | PILC+XLPE | 2024-11-09 19:03:00.000000 UTC | 2024-11-09 19:03 | 11 | 8 | 58 | 2024-11-12 23:42:47.000000 UTC | 131 | 36 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 1 | 3 | Fault Pinpointed at B phase faulty at a distance of 54 meters from Man Niketan Substation Switch Number . Fault pinpointed SREET LIGHT POLE NO BCU098/029 AND LT PILLAR NO.23071623 IN FRONT OF VEDANT PATALOGY LAB,OPPO TO MAN NIKETAN BLDG 2 ,Shown to REDDY. Total length 230 meter. |  | SYSTEM NORMALIZE | 19 | Transition Joint Faulty |  | Fault Details |  | WINTER | 172 | 127 | 127 | 0.74 | 34.14 | 1647 | 0 | 34.47 | 2024-11-12 17:22:42.000000 UTC | PALM COURT REC-STN | 2024-11-09 21:00:49.000000 UTC | Section
1000 |  | 11 KV | MODERATE | JUHU REC-STN | 28490 | HIRANYA | 38117 | 300 | XLPE | 2024-11-27 15:36:42.000000 UTC | 2024-11-27 15:37 | 11 | 1 | 40 | 2024-11-28 18:22:48.000000 UTC | 80 | 0 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 0 | B phase faulty at a distance of 400 meters from Hiranya Substation Switch Number 38117 . Fault pinpointed NS ROAD NO:5KRISHNA NIVAS FRONT GATE. Shown to SAWANT. Total length 790 meter. |  |  | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 93 | 70 | 70 | 0.75 | 31.84 | 1509 | 0 | 30.43 |  | JUHU REC-STN | 2024-11-27 16:20:20.000000 UTC | Section
4000 |  | 11 KV | MODERATE | ANSHUL PLAZA | 39045 | MAHAVIR NAGAR NO.2 | 11787 | 300 | XLPE | 2024-11-27 14:46:00.000000 UTC | 2024-11-27 14:46 | 11 | 5 | 40 | 2024-11-28 23:19:36.000000 UTC | 100 | 15 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 3 | 3 | Y Phase Faulty at 373 Meters from MAHAVIR NAGAR NO.2 Fault Pinpointed at INFRONT OF ANSHUL PLAZA BLDG'S NAME BOARD ON PADMA NGR ROAD Total length : 498 Meters. |  |  | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 100 | 15:30:00 | 85 | 0.85 | 30.43 | 1509 | 0 | 31.84 |  | RNA ROYAL PARK REC-STN | 2024-11-27 16:16:01.000000 UTC | Section
4000 |  | 11 KV | MODERATE | ANUKSHA | 14217 | MAHAVIR NAGAR NO.1 | 19724 | 240+300 | PILC+XLPE | 2024-11-27 16:44:00.000000 UTC | 2024-11-27 16:44 | 11 | 3 | 40 | 2024-11-30 23:59:24.000000 UTC | 130 | 50 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 0 | Fault Pinpointed at y phase faulty at a distance of 26 mtrs from anuksha s/s opposite veena sargam building total length 252 mtrs shown to santosh |  |  | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 129 | 15:10:00 | 105 | 0.81 | 31.84 | 1509 | 0 | 30.43 |  | HIRANANDANI HERITAGE RECEIVING STATION | 2024-11-27 17:36:04.000000 UTC | Section
6000 |  | 11 KV |  | KOHINOOR COMMERCIAL NO.1 | 34395 |  |  |  |  | 2024-10-10 13:09:00.000000 UTC | 2024-10-10 13:09 | 10 |  | 88 | [10 empty] | SYSTEM NORMALIZE | 57 | HT Consumer Network Problem |  | Fault Details | [10 empty] | 2024-10-22 20:19:56.000000 UTC | KOHINOOR COMMERCIAL NO.1 | 2024-10-10 14:47:45.000000 UTC | HT Consumer
3000 |  | 11 KV |  | AAREY GUEST HOUSE KIOSK NO.2 | 17175 |  |  |  |  | 2024-10-10 21:00:14.000000 UTC | 2024-10-10 21:00 | 10 |  | 88 | [10 empty] | SYSTEM NORMALIZE | 57 | HT Consumer Network Problem |  | Fault Details | [10 empty] | 2024-10-13 08:35:07.000000 UTC | AAREY GUEST HOUSE KIOSK NO.2 | 2024-10-10 22:39:23.000000 UTC | HT Consumer
4000 |  | 11 KV | MODERATE | DAHISAR WEST NO.2 | 6991 | SWAYAM NIKETAN | 38981 | 300 | XLPE | 2024-10-22 15:29:00.000000 UTC | 2024-10-22 15:29 | 10 | 2 | 76 | 2024-10-25 02:41:06.000000 UTC | 98 | 80 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 1 | 1 | R Phase Faulty at 524 Meters from DAHISAR WEST NO.2 Fault Pinpointed at NEAR STL POLE NO. RFU017/044 ON RAMCHANDRA PAWEASKAR ROAD (ASPHALT). Total length : 900 Meters. |  |  | 1 | Running Cable Fault |  | Fault Details |  | MONSOON | 68 | 57 | 57 | 0.84 | 48.21 | 1961 | 0 | 34.56 |  | DAHISAR WEST REC-STN | 2024-10-22 15:43:10.000000 UTC | Section
4000 |  | 11 KV | CRITICAL | SUKUR WADI | 38696 | DWARKA APARTMENT | 28725 | 240 | PILC | 2024-10-22 19:24:00.000000 UTC | 2024-10-22 19:24 | 10 | 4 | 76 | 2024-10-26 05:38:49.000000 UTC | 98 | 40 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 1 | 4 | Fault Pinpointed at R PHASE FAULTY AT A DISTANCE OF 243 MTR FROM SUKURWADI CSS FPP NEAR MITTEL PATEL CHOWL SHOWN TO SANTOSH TOTAL |  |  | 19 | Transition Joint Faulty |  | Fault Details |  | MONSOON | 107 | 81 | 81 | 0.76 | 48.21 | 1961 | 0 | 34.56 |  | BORIVALI REC-STN | 2024-10-22 20:23:23.000000 UTC | Section
1000 | VANDRE | 11 KV | MODERATE | EXOTICA | 38465 | JUHU TARA NO.2 | 36926 | 300 | XLPE | 2024-10-22 14:28:05.000000 UTC | 2024-10-22 14:28 | 10 | 2 | 76 | 2024-10-23 22:02:34.000000 UTC | 190 | 160 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 2 | 5 | Y Phase Faulty at 120 Meters from JUHU TARA NO.2 Fault Pinpointed at INFRONT JUHU APPT. GATE. Total length : 292 Meters. |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | SUMMER | 193 | 140 | 140 | 0.73 | 34.56 | 1961 | 0 | 48.21 | 2024-10-23 14:52:55.000000 UTC | SARASWATI RD. REC-STN | 2024-10-22 15:24:17.000000 UTC | Section
5000 |  | 11 KV | MODERATE | VINU INDUSTRIES | 36158 | KASTURI ESTATE NO 1 | 32850 | 240+300 | PILC+XLPE | 2024-10-22 14:11:00.000000 UTC | 2024-10-22 14:11 | 10 | 1 | 76 | 2024-10-25 02:42:34.000000 UTC | 134 | 134 | 0 | 134 | NO EXCAVATION ALONG THE ROUTE | 4 | 0 | Fault Pinpointed at Y phase faulty at a distance of 208 meters from --Select-- Switch Number 32850 . Fault pinpointed ON GHODEO PHATAK ROAD BEFORE GANESH MANDIR OPPO. A1 IND. ESTATE CSS.. |  |  | 1 | Running Cable Fault |  | Fault Details |  | MONSOON | 177 | 108 | 108 | 0.61 | 48.21 | 1961 | 0 | 34.56 |  | BHAYANDAR REC-STN | 2024-10-22 19:21:45.000000 UTC | Section
4000 |  | 11 KV | MODERATE | SHIVALAYA APARTMENT | 18122 | SANSKRUTI | 30230 | 120+150 | PILC+XLPE | 2024-10-21 10:52:00.000000 UTC | 2024-10-21 10:52 | 10 | 6 | 77 | 2024-10-24 11:50:32.000000 UTC | 73 | 40 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 3 | Fault Pinpointed at R phase faulty at a distance of 102 meters from Sanskruti Substation Switch Number 30230 . Fault pinpointed inside private property, near sanzi hotel, on link road, dahisar east. Shown to shinu. Total length 380 meter. |  | SYSTEM NORMALIZE | 4 | Fault Bypassed |  | Fault Details |  | MONSOON | 88 | 22:49:00 | 50 | 0.57 | 35 | 1878 | 0 | 46.86 | 2024-10-22 19:18:34.000000 UTC | DAHISAR WEST REC-STN | 2024-10-21 11:47:00.000000 UTC | Section
6000 |  | 11 KV | MODERATE | ISHA STEEL | 4889 | VARDHMAN WARE HOUSE | 10475 | 185+225+300 | PILC+XLPE | 2024-09-24 12:50:00.000000 UTC | 2024-09-24 12:50 | 9 | 2 | 104 | 2024-09-26 23:38:09.000000 UTC | 150 | 130 | 35 | 1 | NO EXCAVATION ALONG THE ROUTE | 5 | 0 | Faulty at 112 Meters from VARDHMAN WARE HOUSE Fault Pinpointed at VARDHAMAN COMPLEX GATE ON LBS ROAD. Total length : 272 Meters. |  |  | 19 | Transition Joint Faulty |  | Fault Details |  | MONSOON | 174 | 12:07:00 | 107 | 0.61 | 30.32 | 1785 | 58.5 | 43.03 |  | HCC REC-STN | 2024-09-24 16:10:23.000000 UTC | Section
2000 |  | 22 KV | CRITICAL | TATA''S SAKI REC-STN | T22SAKOG10 | CHAKALA REC-STN | 1289 | 300+400 | XLPE | 2024-09-24 21:15:00.000000 UTC | 2024-09-24 21:15 | 9 |  | 104 | 2024-10-05 23:43:44.000000 UTC | 74 |  |  |  |  | 12 |  | No-Fault after testing. All three phases stood ok at KV for Mins. Total Length meters. Remarks |  | SYSTEM NORMALIZE | 19 | Transition Joint Faulty |  | Fault Details | 22kV Cable fault | [9 empty] | 2024-10-05 07:32:23.000000 UTC | TATA''S SAKI REC-STN | 2024-09-24 21:27:20.000000 UTC | Incommer Line
1000 | VANDRE | 33 KV | CRITICAL | TATA''S DHARAVI REC-STN | T33DHAOG11H20 | SANTACRUZ REC-STN | 33128 | 400 | XLPE | 2024-11-15 15:06:17.000000 UTC | 2024-11-15 15:06 | 11 |  | 52 | 2024-11-17 17:00:32.000000 UTC | 175 |  |  |  | NO EXCAVATION ALONG THE ROUTE | 22 |  | Y phase faulty at a distance of 642 meters from Santacruz R/S Switch Number 33128 . Fault pinpointed ON SERVICE ROAD WEH NEAR METRO LIFT FRONT OF HANUMAN TEKDI GATE NO. 1. Shown to sharad. Total length 7200 meter. |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details | 33kV Cable fault | [9 empty] | 2024-11-17 01:10:04.000000 UTC | TATA''S DHARAVI REC-STN | 2024-11-15 15:18:35.000000 UTC | Incommer Line
3000 |  | 11 KV | MODERATE | CHINCH BUNDER REC-STN | 25356 | CELESTIA HEIGHT | 25991 | 400 | XLPE | 2024-11-15 11:11:00.000000 UTC | 2024-11-15 11:11 | 11 | 1 | 52 | 2024-11-16 23:52:58.000000 UTC | 50 | 50 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 3 |  |  |  | 22 | Cable Damaged |  | Fault Details |  | WINTER | 58 | 16:20:00 | 41 | 0.71 | 33.24 | 1726 | 0 | 40.77 |  | CHINCH BUNDER REC-STN | 2024-11-15 11:59:56.000000 UTC | Section
6000 | POWAI | 11 KV | MODERATE | CHANDIVALI GODREJ URBAN PARK | 42632 | R.K.POLYMER | 15627 | 120+300 | PILC+XLPE | 2024-10-19 15:58:00.000000 UTC | 2024-10-19 15:58 | 10 | 3 | 79 | 2024-10-23 06:16:44.000000 UTC | 27 | 25 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE |  | 1 | Y Phase Faulty at 267 Meters from R.K.POLYMER Fault Pinpointed at ON VIJAY FIRE ROAD , NEAR DHANLAXMI TYRE SHOP. Total length : 1178 Meters. |  | SYSTEM NORMALIZE | 4 | Fault Bypassed |  | Fault Details |  | WINTER | 32 | 17:54:00 | 22 | 0.69 | 35.89 | 1856 | 1.25 | 48.98 | 2024-10-20 19:07:54.000000 UTC | CHANDIVLI SRA REC-STN | 2024-10-19 18:49:14.000000 UTC | Section
3000 |  | 11 KV |  | MALAD REC-STN | 29564 |  |  |  |  | 2024-10-05 01:52:00.000000 UTC | 2024-10-05 01:52 | 10 |  | 93 | [11 empty] | 12 | Busbar Flashover |  | Fault Details | [11 empty] | MALAD REC-STN | 2024-10-06 08:35:20.000000 UTC | Busbar and Circuit
1000 |  | 11 KV | CRITICAL | ST FRANCIS ROAD | 13954 | CHURCH ROAD | 6205 | 225+300 | PILC+XLPE | 2024-11-13 19:51:00.000000 UTC | 2024-11-13 19:51 | 11 | 4 | 54 | 2024-11-18 21:35:11.000000 UTC | 91 | 22 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 3 | 1 |  |  | SYSTEM NORMALIZE | 22 | Cable Damaged |  | Fault Details | LOAD CURTAILMENT FOR (N-2) SYSTEM | WINTER | 112 | 90 | 90 | 0.8 | 34.39 | 1710 | 0 | 36.11 | 2024-11-14 19:09:28.000000 UTC | SHRADDHANAND ROAD REC-STN | 2024-11-13 20:34:20.000000 UTC | Section
7000 |  | 11 KV | MODERATE | SAIDEEP | 26990 | LITTLE MALABAR HILL | 32491 | 240+300 | PILC+XLPE | 2024-11-13 12:55:00.000000 UTC | 2024-11-13 12:55 | 11 | 5 | 54 | 2024-11-15 05:50:28.000000 UTC | 98 | 15 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 1 | Y Phase Faulty at 372 Meters from SAIDEEP CSS Fault Pinpointed at FPP ON LAL DONGAR INTERNAL ROAD OPPOSITE LAL DONGAR VAIBHAV CSS, NEAR PEOPLE TREE Total length : 759 Meters. |  | SYSTEM NORMALIZE | 4 | Fault Bypassed |  | Fault Details |  | WINTER | 126 | 100 | 100 | 0.79 | 34.3 | 1710 | 0 | 36.11 | 2024-11-15 18:47:07.000000 UTC | CHUNABHATTI REC-STN | 2024-11-13 14:21:19.000000 UTC | Section
3000 |  | 11 KV | CRITICAL | GORASWADI ROAD NO.2 | 37911 | ADARSH VIHAR | 11856 | 300 | XLPE | 2024-11-13 13:21:00.000000 UTC | 2024-11-13 13:21 | 11 | 2 | 54 | 2024-11-14 13:52:07.000000 UTC | 115 | 110 | 50 | 1 | NO EXCAVATION ALONG THE ROUTE |  | 1 | R phase faulty at a distance of 288 meters from Adarsh Vihar Substation Switch Number 11856 . Fault pinpointed OPP. SIDE OF GIRI APPT. ON GORASHWADI ROAD. Shown to MUTTU. Total length 656 meter. |  |  | 1 | Running Cable Fault |  | Fault Details | LOAD CURTAILMENT FOR (N-2) SYSTEM | WINTER | 155 | 80 | 80 |  |  |  | 0 |  |  | MALAD REC-STN | 2024-11-13 13:50:17.000000 UTC | Section
6000 |  | 11 KV | CRITICAL | HCC REC-STN | 31276 | ASHA 1 | 5864 | 300 | XLPE | 2024-11-13 05:53:00.000000 UTC | 2024-11-13 05:53 | 11 | 1 | 54 | 2024-11-15 06:32:37.000000 UTC | 56 | 56 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 2 | 1 | RY phase faulty at a distance of 708 meters from Hcc R/S Switch Number 31276 . Fault pinpointed ON LBS RD , NEAR MCGM BUS STOP . Shown to SHINU . Total length 1773 meter. |  | SYSTEM NORMALIZE | 4 | Fault Bypassed |  | Fault Details | PRIME AREA | WINTER | 80 | 16:15:00 | 56 | 0.7 | 34.1 | 1710 | 0 | 36.3 | 2024-11-14 19:33:00.000000 UTC | HCC REC-STN | 2024-11-13 06:24:08.000000 UTC | Section
3000 | MALAD | 33 KV | CRITICAL | 220kV VERSOVA REC-STN | 220VER63 | OSHIWARA RECEIVING STATION | 33294 | 400 | XLPE | 2024-11-19 01:57:59.000000 UTC | 2024-11-19 01:58 | 11 |  | 48 | 2024-11-29 23:10:21.000000 UTC | 35 |  |  |  | NO EXCAVATION ALONG THE ROUTE | 6 |  | Fault Pinpointed at B phase faulty at a distance of 1450 meters from Oshiwara Receiving Station Switch Number . Fault pinpointed LINK ROAD OPPOS GOREGAON BUS DEPOT NEAR GANESH GENERAL STORE. Shown to MUTTHU . Total length 4910 meter. |  | SYSTEM NORMALIZE | 23 | Straight Joint Faulty |  | Fault Details | 33kV Cable fault | [9 empty] | 2024-11-27 20:28:06.000000 UTC | 220kV VERSOVA REC-STN | 2024-11-19 02:01:31.000000 UTC | Incommer Line
3000 |  | 11 KV | MODERATE | SATYAM SOCIETY | 34782 | SINGH ESTATE NO.1 | 4787 | 240+300 | PILC+XLPE | 2024-11-19 15:42:00.000000 UTC | 2024-11-19 15:42 | 11 | 2 | 48 | 2024-11-22 23:38:01.000000 UTC | 150 | 0 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 3 | 0 | Fault Pinpointed at B PHASE FAULTY AT A DISTANCE OF 242 METERS FR...OM SATYAM SOCIETY SUBSTATION SWITCH NUMBER 34782 . FAULT PINPOINTED NR BHATTI CHANNEL WORK CONSTRUCTION, RAM MANDIR RD. SHOWN TO MUTTHU. TOTAL LENGTH 397 METER. |  |  | 4 | Fault Bypassed |  | Fault Details |  | WINTER | 170 | 12:00:00 | 140 | 0.82 | 33.31 | 1658 | 0 | 33.05 |  | GOREGAON REC-STN | 2024-11-19 16:36:50.000000 UTC | Section
2000 |  | 11 KV | MODERATE | YAMUNA NAGAR NO.3 | 14017 | ST.LAURENCE SCHOOL | 31607 | 120+150 | PILC+XLPE | 2024-11-18 11:29:00.000000 UTC | 2024-11-18 11:29 | 11 | 6 | 49 | 2024-11-19 23:08:15.000000 UTC | 54 | 12 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 3 | 4 | B phase faulty at a distance of 108 meters from St.Laurence School Substation Switch Number 31607 . Fault pinpointed YAMUNA NGR RD, NEAR GREEN CREST CHS. . Shown to YADYA. Total length 365 meter. |  |  | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 61 | 47.5 | 47.5 | 0.78 | 34.44 | 1716 | 0 | 36.13 |  | VERSOVA RECEIVING STATION | 2024-11-18 13:05:11.000000 UTC | Section
2000 |  | 11 KV | MODERATE | SATYA DARSHAN | 11965 | ANUPAM | 6023 | 120 | PILC | 2024-11-18 11:41:00.000000 UTC | 2024-11-18 11:41 | 11 | 3 | 49 | 2024-11-22 23:15:23.000000 UTC | 155 | 83 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 2 | 4 | YB phase faulty at a distance of 180 meters from Anupam Substation Switch Number 6023 . Fault pinpointed ON DATTA JAGDAMBA MANDIR MARG, RADHA KRISHNA NAGAR. Shown to YADYA. Total length 410 meter. |  |  | 19 | Transition Joint Faulty |  | Fault Details |  | WINTER | 161 | 15:54:00 | 104 | 0.65 | 36.13 | 1716 | 0 | 34.44 |  | HINDUSTAN UNILEVER REC-STN | 2024-11-18 13:14:17.000000 UTC | Section
7000 |  | 11 KV | MODERATE | MANDALA METRO CARSHED | 42837 | MHADA MANKHURD | 34980 | 300+400 | XLPE | 2024-11-18 16:57:00.000000 UTC | 2024-11-18 16:57 | 11 | 2 | 49 | 2024-11-22 23:30:43.000000 UTC | 37 | 35 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 3 | 2 | B Phase Faulty at 115 Meters from MANDALA METRO CARSHED Fault Pinpointed at Fault pinpointed FAULT NEAR CULVERT NEW METRI BUILDING IN METRO CARSHED. |  |  | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 67 | 59 | 59 | 0.88 | 34.44 | 1716 | 0 | 36.13 |  | MHADA MANKHURD RECEIVING STATION | 2024-11-18 17:46:06.000000 UTC | Section
3000 |  | 11 KV | MODERATE | KHETAN HOUSING | 38350 | MAMLEDAR WADI ROAD NO.2 | 35589 | 300 | XLPE | 2024-11-18 23:03:00.000000 UTC | 2024-11-18 23:03 | 11 | 3 | 49 | 2024-11-23 23:57:11.000000 UTC | 127 | 112 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 9 | 3 | Y Phase Faulty at 188 Meters from MAMLEDAR WADI ROAD NO.2 Fault Pinpointed at INSIDE CHAMBER NEAR Vishwakarma kunj opp akabishhi metro cell shown to lingya Total length : 650 Meters. |  |  | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 135 | 107.5 | 107.5 | 0.8 | 34.44 | 1716 | 0 | 36.13 |  | MALAD REC-STN | 2024-11-19 00:01:00.000000 UTC | Section
3000 |  | 11 KV | MODERATE | MUKADAM COMPOUND NO.2 | 42980 | SWAPNALOK | 29405 | 150+300 | XLPE | 2024-11-19 18:44:00.000000 UTC | 2024-11-19 18:44 | 11 | 5 | 48 | 2024-11-20 23:21:47.000000 UTC | 110 | 50 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 2 | 0 | B Phase Faulty at 89 Meters from SWAPNALOK Fault Pinpointed at FPP NEAR SAI VAISHNAV INFRASTRUCTURE OFFICE ON RANI SATI MARG,TOTAL LENGTH 205 MTR, SHOWN TO MR. MUTTU. Total length : 205 Meters. |  |  | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 120 | 11:00:00 | 90 | 0.75 | 33.31 | 1658 | 0 | 33.05 |  | GOKULDHAM REC-STN | 2024-11-19 19:39:07.000000 UTC | Section
6000 | POWAI | 33 KV | CRITICAL | 220 kV AAREY EHV STATION | 220AAR58 | KOHINOOR RECEIVING STATION | 33353 | 400 | PILC | 2024-10-03 02:52:00.000000 UTC | 2024-10-03 02:52 | 10 | 1 | 95 |  | 0 | 0 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE |  | 0 | Y Phase Faulty at 3348 Meters from 220 kV AAREY EHV STATION Fault Pinpointed at ON AK ROAD NEAR BATA SHOWROOM AHEAD OF CULVERT |  | SYSTEM NORMALIZE | 23 | Straight Joint Faulty |  | Fault Details | 33kV Cable fault | [9 empty] | 2024-11-11 22:35:26.000000 UTC | 220 kV AAREY EHV STATION | 2024-10-03 08:58:06.000000 UTC | Incommer Line
7000 |  | 11 KV | MODERATE | BAINGANWADI 2 | 13504 | BAINGANWADI 1 | 12212 | 120+300 | XLPE | 2024-10-03 05:16:00.000000 UTC | 2024-10-03 05:16 | 10 | 3 | 95 | 2024-10-04 07:18:36.000000 UTC | 80 | 0 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 2 | 1 | B Phase Faulty at 102 Meters from BAINGANWADI 2 Fault Pinpointed at Fault pinpointed on rd 12 bainganwadi , near JAMJAM TELEPHONE SHOP, OPPO MASJID RAHMATI ALAM , BAINGANWADI . Total length : 304 Meters. |  | SYSTEM NORMALIZE | 4 | Fault Bypassed |  | Fault Details |  | MONSOON | 107 | 12:11:00 | 70 | 0.65 | 33.33 | 1911 | 0 | 52.33 | 2024-10-04 20:14:59.000000 UTC | SHIVAJI NAGAR REC-STN | 2024-10-03 05:59:47.000000 UTC | Section
6000 |  | 11 KV | MODERATE | LAXMI NGR SNEH SADAN | 42086 | LAXMI NGR 4 | 28855 | 300 | XLPE | 2024-11-20 14:34:00.000000 UTC | 2024-11-20 14:34 | 11 | 3 | 47 | 2024-11-20 02:14:25.000000 UTC | 25 | 14 | 0 | 0 | EXCAVATION ALONG THE ROUTE |  | 2 |  |  | SYSTEM NORMALIZE | 22 | Cable Damaged |  | Fault Details |  | WINTER | 74 | 19:32:00 | 43 | 0.58 | 33.3 | 1658 | 0 | 33.05 | 2024-11-20 23:05:51.000000 UTC | VIKHROLI REC-STN | 2024-11-20 15:14:45.000000 UTC | Section
2000 |  | 11 KV | MODERATE | WINDERMERE | 19147 | ANAND NO.4 | 19576 | 120 | PILC | 2024-10-20 12:06:00.000000 UTC | 2024-10-20 12:06 | 10 | 5 | 78 | 2024-10-21 15:58:40.000000 UTC | 100 | 85 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 2 | 2 | Y Phase Faulty at 400 Meters from WINDERMERE Fault Pinpointed at OPPOSITE OF MINIPILLAR 19070504, NEAR BEAUTYGLOW SALOON, ON LINK ROAD Total length : 476 Meters. |  |  | 1 | Running Cable Fault |  | Fault Details |  | MONSOON | 145 | 14:58:00 | 107 | 0.74 | 34.03 | 1612 | 0.25 | 47.91 |  | VERSOVA RECEIVING STATION | 2024-10-20 15:27:56.000000 UTC | Section
1000 |  | 11 KV | MODERATE | GDC HOUSE NO.2 | 37544 | MAHESH CHS | 37540 | 300 | XLPE | 2024-10-20 22:35:37.000000 UTC | 2024-10-20 22:36 | 10 | 6 | 78 | 2024-10-23 23:40:57.000000 UTC | 129 | 80 | 0 | 0 | EXCAVATION ALONG THE ROUTE |  | 4 | B Phase Faulty at 20 Meters from MAHESH CHS Fault Pinpointed at Fault pinpointed CENTRE OF VM ROAD |  |  | 1 | Running Cable Fault |  | Fault Details |  | MONSOON | 184 | 12:32:00 | 150 | 0.82 | 34.03 | 1612 | 0.25 | 47.91 |  | SARASWATI RD. REC-STN | 2024-10-20 23:37:02.000000 UTC | Section
2000 | ANDHERI |  | CRITICAL | TPC SAHAR RECEIVING STATION | T22SHROG11H31 | MIAL T-2 DSS REC-STN | 33348 | 400 | XLPE | 2024-10-26 16:38:00.000000 UTC | 2024-10-26 16:38 | 10 |  | 72 | 2024-10-28 21:11:24.000000 UTC | 68 |  |  |  | NO EXCAVATION ALONG THE ROUTE | 2 |  | B phase faulty at a distance of 1175 meters from Tata Sahar Receiving Station Switch Number OG-11 H31 . Fault pinpointed SAHAR AIRPORT ROIAD BELOW COMPOUND WALL OF FAIRMONT SHREMS.. Shown to PALANY. Total length 1900 meter.PT DISCONNECTED AT MIAL END |  | SYSTEM NORMALIZE | 4 | Fault Bypassed |  | Fault Details | 33kV Cable fault | [9 empty] | 2024-10-28 03:48:12.000000 UTC | TPC SAHAR RECEIVING STATION | 2024-10-27 07:54:43.000000 UTC | Incommer Line
7000 |  | 11 KV |  | TROMBAY RESERVOIR | 32570 |  |  |  |  | 2024-10-26 16:45:00.000000 UTC | 2024-10-26 16:45 | 10 |  | 72 | [10 empty] | SYSTEM NORMALIZE | 57 | HT Consumer Network Problem |  | Fault Details | [10 empty] | 2024-10-27 03:53:19.000000 UTC | TROMBAY RESERVOIR | 2024-10-26 22:08:43.000000 UTC | HT Consumer
6000 |  | 22 KV | CRITICAL | VIKHROLI REC-STN | 1135 | TAGORE NGR. REC-STN | 1102 | 300 |  | 2024-10-25 04:02:00.000000 UTC | 2024-10-25 04:02 | 10 |  | 73 | 2024-10-27 07:48:22.000000 UTC | 120 |  |  |  | NO EXCAVATION ALONG THE ROUTE | 21 |  | Y Phase Faulty at 1920 Meters from TAGORE NGR. REC-STN Fault Pinpointed at FAULT PINPOINTED IN GARDEN NEAR UDAYCHAL PRIMARY SCHOOL IN GODREJ PRIMISES. |  |  | 19 | Transition Joint Faulty |  | Fault Details | 22kV Cable fault | [10 empty] | TATA''S VIKHROLI REC-STN | 2024-10-25 19:31:33.000000 UTC | Incommer Line
6000 |  | 11 KV | CRITICAL | GHATKOPAR HILL 3 | 29238 | GHATKOPAR HILL 2 | 16719 | 300 | XLPE | 2024-10-25 10:24:00.000000 UTC | 2024-10-25 10:24 | 10 | 12 | 73 | 2024-10-25 23:58:00.000000 UTC | 205 | 60 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 2 |  |  |  | 22 | Cable Damaged |  | Fault Details | LOAD CURTAILMENT FOR (N-2) SYSTEM | MONSOON | 240 | 11:59:00 | 189 | 0.79 | 36.62 | 1911 | 0 | 45.25 |  | KURLA REC-STN | 2024-10-25 11:15:05.000000 UTC | Section
3000 | MALAD | 11 KV | MODERATE | MALVANI COLONY NO.5 | 14606 | MALWANI MHADA PUMP | 18331 | 300 | XLPE | 2024-10-25 11:29:00.000000 UTC | 2024-10-25 11:29 | 10 | 2 | 73 | 2024-10-28 03:55:29.000000 UTC | 118 | 68 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 6 | 0 | R Phase Faulty at 558 Meters from MALWANI MHADA PUMP Fault Pinpointed at OPP. SAINA THETAR Total length : 1677 Meters. |  | SYSTEM NORMALIZE | 4 | Fault Bypassed |  | Fault Details |  | WINTER | 117 | 11:39:00 | 86 | 0.74 | 36.62 | 1911 | 0 | 416 | 2024-10-29 01:35:12.000000 UTC | PALM COURT REC-STN | 2024-10-25 13:40:54.000000 UTC | Section
5000 |  | 11 KV | CRITICAL | SHEREY LANE | 25978 | VELANKINI CHURCH | 29114 | 150 | XLPE | 2024-10-25 11:45:16.000000 UTC | 2024-10-25 11:45 | 10 | 14 | 73 | 2024-10-28 23:59:41.000000 UTC | 130 | 10 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 3 | 7 | Fault Pinpointed at Y PHASE FAULTY AT A DISTANCE OF 80 METERS FRO...M VELANKINI CHURCH SUB STATION SWITCH NUMBER 29114 . FAULT PINPOINTED ON VELANKINI CHURCH ROAD, OPP. MAHALAXMI CORNER HOTEL, NEXT TO CHURCH, . SHOWN TO GANGADHAR. TOTAL LENGTH 1580 METER. |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | MONSOON | 174 | 130 | 130 | 0.75 | 31.9 | 1617 | 0 | 41.18 | 2024-10-26 17:13:53.000000 UTC | BHAYANDAR WEST REC-STN | 2024-10-25 11:48:12.000000 UTC | Section
1000 |  | 11 KV |  | PRIME BUSINESS PARK | 36802 | AVON | 10893 |  |  | 2024-11-06 22:41:00.000000 UTC | 2024-11-06 22:41 | 11 |  | 61 | 2024-11-07 00:27:58.000000 UTC | [7 empty] | RY phase faulty at a distance of 70 meters from Prime Business Park Substation Switch Number 36802 . Fault pinpointed ST MARRY RD IN FRONT OF GATE OF PRIME BUSINESS PARK.. Shown to ASHOK. Total length 310 meter. |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 193 | 15:26:00 | 104 | 0.54 | 36.18 | 1782 | 0 | 41.98 | 2024-11-07 06:22:15.000000 UTC | JUHU REC-STN | 2024-11-07 00:25:36.000000 UTC | Section
1000 |  | 11 KV | MODERATE | BADRINATH | 40767 | T K HOTEL | 9016 | 240 | PILC | 2024-11-06 19:51:00.000000 UTC | 2024-11-06 19:51 | 11 | 6 | 61 | 2024-11-09 03:04:44.000000 UTC | 100 | 15 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 10 | 1 | B Phase Faulty at 60 Meters from BADRINATH Fault Pinpointed at 13TH RD NEAR ROYAL ACCORD BUILDING. Total length : 254 Meters. |  | SYSTEM NORMALIZE | 19 | Transition Joint Faulty |  | Fault Details |  | MONSOON | 112 | 18:36:00 | 91 | 0.81 | 36.18 | 1782 | 0 | 41.98 | 2024-11-08 01:33:00.000000 UTC | 24TH ROAD REC-STN | 2024-11-06 21:08:22.000000 UTC | Section
2000 |  | 11 KV | MODERATE | DEEP TOWER | 18982 | M H A D A NO.1 | 12889 | 300 | XLPE | 2024-11-06 15:01:00.000000 UTC | 2024-11-06 15:01 | 11 | 2 | 61 | 2024-11-11 06:52:45.000000 UTC | 87 | 70 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 5 | 0 | No-Fault after testing. All three phases stood ok at KV for Mins. Total Length meters. Remarks |  |  | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 90 | 15:40:00 | 70 | 0.78 | 36.18 | 1382 | 0 | 41.98 |  | VERSOVA RECEIVING STATION | 2024-11-06 16:44:00.000000 UTC | Section
1000 |  | 11 KV | MODERATE | KALINA REC-STN | 35366 | KALINA NORTH NO.2 | 16805 | 225+240+400 | PILC+XLPE | 2024-11-06 13:13:00.000000 UTC | 2024-11-06 13:13 | 11 | 1 | 61 | 2024-11-09 21:15:23.000000 UTC | 43 | 43 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 7 | 1 | RYB Phase Faulty at 290 Meters from KALINA REC-STN Fault Pinpointed at OLD CST ROAD, OPPOSITE SUNFLOWER APPT GATE. Total length : 711 Meters. |  | SYSTEM NORMALIZE | 19 | Transition Joint Faulty |  | Fault Details |  | WINTER | 49 | 26 | 26 | 0.53 | 36.18 | 1782 | 0 | 41.98 | 2024-11-08 01:02:36.000000 UTC | KALINA REC-STN | 2024-11-06 14:36:31.000000 UTC | Section
3000 |  | 11 KV | MODERATE | MAHANANDA REC-STN | 9256 | INDABRATTOR | 9122 | 240 | PILC | 2024-11-06 12:46:00.000000 UTC | 2024-11-06 12:46 | 11 | 1 | 61 | 2024-11-16 23:15:34.000000 UTC | 7 | 7 | 160 | 1 | EXCAVATION ALONG THE ROUTE | 10 | 1 | RYB Phase Faulty at 38 Meters from INDABRATTOR Fault Pinpointed at TRESS NO .179 Total length : 358 Meters. |  |  | 19 | Transition Joint Faulty |  | Fault Details |  | WINTER | 7 | 15:30:00 | 5 | 1 | 36.18 | 1784 | 0 | 41.98 |  | MAHANANDA REC-STN | 2024-11-06 13:12:16.000000 UTC | Section
4000 |  | 11 KV | MODERATE | RSC 52 | 38520 | RSC 34 | 17830 | 120+300 | PILC+XLPE | 2024-10-27 02:58:00.000000 UTC | 2024-10-27 02:58 | 10 | 3 | 71 | 2024-10-29 23:00:49.000000 UTC | 130 | 10 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 1 | RY phase faulty at a distance of 209 meters from Rsc - 52 Sub Station Switch Number 38520 . Fault pinpointed ON RSC-34 ROAD NEAR RSC-34 S/S, BESIDE KARKOP AKHAND SOCIETY. Shown to SANTOSH. Total length 234 meter. |  |  | 1 | Running Cable Fault |  | Fault Details |  | MONSOON | 193 | 00:16:00 | 160 | 0.83 | 34.43 | 1646 | 0.22 | 42.94 |  | RNA ROYAL PARK REC-STN | 2024-10-27 03:58:29.000000 UTC | Section
2000 |  | 11 KV | MODERATE | USHA DARSHAN | 13140 | ANAND NO.3 | 13800 | 120 | PILC | 2024-10-28 01:58:39.000000 UTC | 2024-10-28 01:59 | 10 | 5 | 70 | 2024-10-31 03:05:14.000000 UTC | 99 | 9 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 3 | 4 | RB phase faulty at a distance of 300 meters from Usha Darshan Substation Switch Number 13140 . Fault pinpointed BST COLONY RD IN FRONT OF HAKIM AALIM SALOON.. Shown to YADYA. Total length 1100 meter. |  | SYSTEM NORMALIZE | 19 | Transition Joint Faulty |  | Fault Details |  | MONSOON | 136 | 98 | 98 | 0.72 | 34.73 | 1903 | 0 | 46.34 | 2024-10-29 18:37:36.000000 UTC | VERSOVA RECEIVING STATION | 2024-10-28 02:22:03.000000 UTC | Section
6000 |  | 11 KV | MODERATE | BKC EXCHANGE | 19748 | TAXIMEN CLY 2 | 17150 | 240 | PILC | 2024-10-28 02:24:07.000000 UTC | 2024-10-28 02:24 | 10 | 3 | 70 | 2024-10-30 02:48:41.000000 UTC | 30 | 12 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 2 | 2 | Y Phase Faulty at 91 Meters from TAXIMEN CLY 2 Fault Pinpointed at OPPOSITE TO TAXIMAN CLY GATE ON KURLA BKC ROAD Total length : 876 Meters. |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details |  | MONSOON | 48 | 35 | 35 | 0.73 | 34.73 | 1903 | 0 | 46.34 | 2024-10-29 01:08:13.000000 UTC | MMRDA REC-STN | 2024-10-28 02:43:02.000000 UTC | Section
7000 |  | 11 KV | MODERATE | ANNAPURNA | 2679 | SAI HERITAGE | 30338 | 225+240+300 | PILC+XLPE | 2024-11-08 14:32:00.000000 UTC | 2024-11-08 14:32 | 11 | 7 | 59 | 2024-11-16 23:06:22.000000 UTC | 68 | 30 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 2 | 1 | YB Phase Faulty at 1139 Meters from SAI HERITAGE Fault Pinpointed at ON TILAK ROAD OPPO TO BALAJI MANDIR |  | SYSTEM NORMALIZE | 4 | Fault Bypassed |  | Fault Details |  | WINTER | 80 | 16:00:00 | 60 | 0.75 | 34.39 | 1738 | 0 | 36.2 | 2024-11-16 18:47:37.000000 UTC | HINGWALA LANE REC-STN | 2024-11-08 15:09:20.000000 UTC | Section
7000 |  | 11 KV | MODERATE | BHARAT GLASS | 16729 | MOHAN SADAN | 38270 | 300 | XLPE | 2024-11-08 10:39:00.000000 UTC | 2024-11-08 10:39 | 11 | 3 | 59 | 2024-11-10 12:54:16.000000 UTC | 174 | 15 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 8 | 4 |  |  |  | 22 | Cable Damaged |  | Fault Details |  | WINTER | 190 | 10:57:00 | 135 | 0.71 | 34.39 | 1738 | 0 | 36.22 |  | TILAK NAGAR REC-STN | 2024-11-08 11:22:20.000000 UTC | Section
2000 |  | 11 KV | MODERATE | DEEP TOWER | 18982 | M H A D A NO.1 | 12889 | 300 | XLPE | 2024-11-08 21:56:00.000000 UTC | 2024-11-08 21:56 | 11 | 2 | 59 | 2024-11-11 23:52:08.000000 UTC | 45 | 38 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 6 | 0 | R phase faulty at a distance of 525 meters from Deep Tower Substation Switch Number 18982 . Fault pinpointed TARA PORE GARDEN GATE NO.2 BLDG ESE.. Shown to JANARDHAN. Total length 766 meter. |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 43 | 21:29:00 | 39 | 0.91 | 34.39 | 1738 | 0 | 36.22 | 2024-11-11 22:18:53.000000 UTC | VERSOVA RECEIVING STATION | 2024-11-08 23:04:13.000000 UTC | Section
5000 |  | 11 KV | CRITICAL | NITYANAND DHAM | 10284 | NAVGHAR ROAD NO 2 | 34087 | 120+150 | PILC+XLPE | 2024-11-08 19:35:00.000000 UTC | 2024-11-08 19:35 | 11 | 8 | 59 | 2024-11-12 03:42:10.000000 UTC | 140 | 0 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 2 | 5 | R phase faulty at a distance of 14 meters from Navghar Road No.2 Sub Station Switch Number 34087 . Fault pinpointed NEAR NAVGHAR ROAD NO.2 CSS ON NAVGHAR CROSS ROAD. Shown to SHANKAR. Total length 270 meter. |  |  | 19 | Transition Joint Faulty |  | Fault Details | MORE THAN 5 RADIAL SUBSTATIONS | WINTER | 160 | 18:29:00 | 130 | 0.81 | 34.39 | 1738 | 0 | 36.22 |  | BHAYANDAR REC-STN | 2024-11-08 20:48:00.000000 UTC | Section
3000 |  | 11 KV | MODERATE | A.K. PLAZA | 28393 | UDYOG NAGAR NO.1 | 5109 | 240+300 | PILC+XLPE | 2024-11-08 11:49:00.000000 UTC | 2024-11-08 11:49 | 11 | 4 | 59 | 2024-11-12 12:50:27.000000 UTC | 74 | 50 | 0 | 0 | EXCAVATION ALONG THE ROUTE |  | 1 | Fault Pinpointed at YB phase faulty at a distance of 213 meters from Udyog Nagar No.1 Substation Switch Number . Fault pinpointed UDYOG NAGAR ROAD NEAR IMPERIAL BANQUET. . Shown to MUTHU. Total length 336 meter. |  | SYSTEM NORMALIZE | 2 | Casting Joint Faulty |  | Fault Details |  | WINTER | 84 | 15:25:00 | 58 | 0.69 | 34.39 | 1738 |  | 36.22 | 2024-11-09 20:53:32.000000 UTC | CHINCHAVLI REC-STN | 2024-11-08 12:40:55.000000 UTC | Section
1000 |  | 11 KV | MODERATE | KALINA REC-STN | 35372 | KALINA GLORIA | 41831 | 240+300 | PILC+XLPE | 2024-10-15 16:12:00.000000 UTC | 2024-10-15 16:12 | 10 | 1 | 83 | 2024-10-16 07:24:50.000000 UTC | 160 | 160 | 30 | 0 | EXCAVATION ALONG THE ROUTE |  | 1 | RY Phase Faulty at 310 Meters from KALINA REC-STN Fault Pinpointed at KALINA KURLA RD OPPOSITE MAHESH JWELLERS Total length : 560 Meters. |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details | LOAD CURTAILMENT FOR (N-2) SYSTEM | MONSOON | 165 | 15:15:00 | 132 | 0.8 | 33.04 | 1853 | 6 | 44.86 | 2024-10-17 03:26:58.000000 UTC | KALINA REC-STN | 2024-10-15 20:34:42.000000 UTC | Section
7000 |  | 11 KV | CRITICAL | PANVEL RD 3 | 37510 | L &T VASHI BRIDGE | 41922 | 300 | XLPE | 2024-10-15 20:09:00.000000 UTC | 2024-10-15 20:09 | 10 | 7 | 83 | 2024-10-16 02:45:53.000000 UTC | 81 | 5 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 1 | 1 | Y Phase Faulty at 60 Meters from L &T VASHI BRIDGE Fault Pinpointed at Inside premises of l&t washi bridge infront of consumer dg set Total length : 500 Meters. |  | SYSTEM NORMALIZE | 1 | Running Cable Fault |  | Fault Details | SUBSTATIONS ARE AFFECTED | MONSOON | 83 | 08:23:00 | 70 | 0.84 | 33.04 | 1853 | 6 | 45.86 | 2024-10-16 13:04:45.000000 UTC | MHADA MANKHURD RECEIVING STATION | 2024-10-15 21:16:39.000000 UTC | Section
4000 |  | 11 KV | MODERATE | RAM NAGAR | 38910 | DWARKESH PARK | 17877 | 120+300 | PILC+XLPE | 2024-09-22 09:23:00.000000 UTC | 2024-09-22 09:23 | 9 | 3 | 106 | 2024-09-25 23:17:49.000000 UTC | 53 | 20 | 0 | 1 | NO EXCAVATION ALONG THE ROUTE | 1 | 1 | R Phase from DWARKESH PARK |  |  | 19 | Transition Joint Faulty |  | Fault Details |  | MONSOON | 61 | 20:40:00 | 45 | 0.74 | 31.82 | 1573 | 0 | 44.23 |  | HIRANANDANI HERITAGE RECEIVING STATION | 2024-09-22 10:44:29.000000 UTC | Section
3000 |  | 11 KV | MODERATE | MARVE ROAD NO.3 | 6078 | GREAT EASTERN HEIGHT | 17081 | 240+300 | PILC+XLPE | 2024-11-24 14:54:00.000000 UTC | 2024-11-24 14:54 | 11 | 6 | 43 | 2024-11-27 07:36:32.000000 UTC | 73 | 30 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 3 | 0 | Y Phase Faulty at 298 Meters from GREAT EASTERN HEIGHT Fault Pinpointed at CHUNILAL GIRDHARILAL ROAD. Shown to MUTTHU Total length : 616 Meters. |  |  | 4 | Fault Bypassed |  | Fault Details |  | WINTER | 84 | 11:09:00 | 65.5 | 0.78 | 32.5 | 1343 | 0 | 34.36 |  | GANESH NAGAR MHADA REC-STN | 2024-11-24 15:18:52.000000 UTC | Section
4000 |  | 11 KV | MODERATE | KASTUR PARK NO 1 | 6145 | SILVER LINE | 10041 | 240+300 | PILC+XLPE | 2024-11-24 09:26:00.000000 UTC | 2024-11-24 09:26 | 11 | 5 | 43 | 2024-11-28 07:40:03.000000 UTC | 97 | 30 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE |  | 3 | Fault Pinpointed at B PHASE FAULTY AT DISTANCE OF 53 MTRS FROM SILVERLINE S/S FPP AT THE GATE OF SILVERLINE APARTMENT 6 MTRS AWAY FROM PILLAR 27090711 TOTAL LENGTH 493 MTRS SHOWN TO NARESH |  |  | 19 | Transition Joint Faulty |  | Fault Details |  | WINTER | 162 | 10:40:00 | 101 | 0.62 | 32.5 | 1343 | 0 | 34.36 |  | VAZIRA REC-STN | 2024-11-24 10:44:40.000000 UTC | Section
4000 |  | 11 KV | MODERATE | KASTURBA ROAD HOSPITAL | 40770 | GURU KRIPA | 5499 | 240+300 | PILC+XLPE | 2024-11-24 00:51:00.000000 UTC | 2024-11-24 00:51 | 11 | 8 | 43 | 2024-11-27 07:50:20.000000 UTC | 66 | 20 | 0 | 2 | EXCAVATION ALONG THE ROUTE | 1 | 3 | B Phase Faulty at 310 Meters from KASTURBA ROAD HOSPITAL Fault Pinpointed at OUTSIDE TULSI BLDG 2ND (OUT) GATE NEAR DRAIN WORKS. Total length : 464 Meters. |  |  | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 92 | 10:48:00 | 74 | 0.8 | [5 empty] | KANAKIA CCI REC-STN | 2024-11-24 02:34:27.000000 UTC | Section
2000 |  | 11 KV | MODERATE | UNANI MEDICAL COLLEGE | 18742 | JUBILEE ABAD BAUG APARTMENT | 15570 | 120 | PILC | 2024-11-24 14:16:40.000000 UTC | 2024-11-24 14:17 | 11 | 3 | 43 | 2024-11-25 18:18:57.000000 UTC | 157 | 30 | 0 | 0 | EXCAVATION ALONG THE ROUTE |  | 0 | RYB phase faulty at a distance of 219 meters from Unani Medical College Substation Switch Number 18742 . Fault pinpointed OPPOSITE EMERAL BUIDING ON D MART ROAD, . Shown to GANESH. Total length 392 meter. |  |  | 1 | Running Cable Fault |  | Fault Details |  | MONSOON | 219 | 18:28:54 | 171 | 0.78 | 32.5 | 1343 | 0 | 34.36 |  | VERSOVA RECEIVING STATION | 2024-11-24 14:56:58.000000 UTC | Section
3000 |  | 11 KV | MODERATE | SHREEJI DARSHAN | 10630 | MILAP | 36193 | 0.06+70+300 | PILC+XLPE | 2024-11-24 02:48:00.000000 UTC | 2024-11-24 02:48 | 11 | 4 | 43 | 2024-11-28 23:02:34.000000 UTC | 44 | 5 | 0 | 0 | EXCAVATION ALONG THE ROUTE |  | 1 | Y phase faulty at a distance of 60 meters from Shreeji Darshan Substation Switch Number 10630 . Fault pinpointed NEAR BATA SHOWROOM OPPOSITE KHM HOSIPATL . Shown to LINGAYA . Total length 698 meter. |  |  | 4 | Fault Bypassed |  | Fault Details |  | WINTER | 80 | 70 | 70 | 0.88 |  |  | 0 |  |  | KANDIVLI REC-STN | 2024-11-24 03:43:45.000000 UTC | Section
3000 |  | 11 KV | MODERATE | KALPATARU RADIANCE | 39272 | GOREGAON REC-STN | 1534 | 240+300 | PILC+XLPE | 2024-11-24 12:11:00.000000 UTC | 2024-11-24 12:11 | 11 | 4 | 43 | 2024-11-28 07:33:08.000000 UTC | 25 | 0 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE | 1 | 3 | Y Phase Faulty at 434 Meters from KALPATARU RADIANCE Fault Pinpointed at Fault pinpointed SIDDHARTH NGR RD NO.10, NEAR POLE NO. TCD/063/035, Total length : 770 Meters. |  |  | 4 | Fault Bypassed |  | Fault Details |  | WINTER | 35 | 14:15:00 | 27.5 | 0.79 | 32.5 | 1343 | 0 | 34.36 |  | OSHIWARA RECEIVING STATION | 2024-11-24 14:49:55.000000 UTC | Section
6000 |  | 11 KV | MODERATE | SAKI REC-STN | 3104 | SAKI NAKA 1 | 6857 | 300 | XLPE | 2024-10-17 22:25:56.000000 UTC | 2024-10-17 22:26 | 10 | 1 | 81 | 2024-10-20 07:17:17.000000 UTC | 173 | 173 | 0 | 0 | NO EXCAVATION ALONG THE ROUTE |  | 1 | Y Phase Faulty at 545 Meters from SAKI NAKA 1 Fault Pinpointed at 5 MTR FROM CONSUMER CENTRE GATE (SAKI NAKA REC ) TOWARDS ANDHERI SIDE. Total length : 566 Meters. |  |  | 23 | Straight Joint Faulty |  | Fault Details |  | SUMMER | 200 | 160 | 160 | 0.8 | 32.23 | 1899 | 0 | 52.07 |  | SAKI REC-STN | 2024-10-17 23:51:39.000000 UTC | Section
4000 |  | 11 KV | MODERATE | GORAI RSC 52 | 16641 | GORAI RSC 52 SOUTH | 17241 | 120 | PILC | 2024-11-23 14:37:00.000000 UTC | 2024-11-23 14:37 | 11 | 3 | 44 | 2024-11-25 18:50:45.000000 UTC | 41 | 20 | 0 | 1 | EXCAVATION ALONG THE ROUTE | 1 | 2 | Fault Pinpointed at R PHASE FAULTY AT A DISTANCE OF 45 MTRS FROM GORAI RSC 52 NEAR 6 WAY PILLAR IN FRONT OF SHOP 4 SHOWN TO SANTOSH TOTAL LENGTH 250 MTRS |  |  | 1 | Running Cable Fault |  | Fault Details |  | WINTER | 70 | 12:00:00 | 50 | 0.71 | 33.28 | 1541 | 0 | 35.72 |  | GORAI REC-STN | 2024-11-23 15:39:59.000000 UTC | Section
2000 |  | 11 KV | CRITICAL | WRITER HOUSE | 18417 | MAROL CHURCH ROAD NO.2 | 13092 | 120 | PILC | 2024-11-23 11:42:00.000000 UTC | 2024-11-23 11:42 | 11 | 5 | 44 | 2024-11-24 00:12:46.000000 UTC | 83 | 33 | 0 | 1 | EXCAVATION ALONG THE ROUTE | 1 | 4 | RYB phase faulty at a distance of 140 meters from Marol Church Road No.2 Substation Switch Number 13092 . Fault pinpointed ON MAROL CHURCH ROAD. 5 MTR AWAY FROM LT PILLAR NO 15111403.. Shown to GANESH. Total length 209 meter. |  | SYSTEM NORMALIZE | 4 | Fault Bypassed |  | Fault Details | LOAD CURTAILMENT FOR (N-2) SYSTEM | WINTER | 105 | 19:03:00 | 88 | 0.84 | 33.04 | 1611 | 0 | 33.96 | 2024-11-24 18:17:38.000000 UTC | SAKI REC-STN | 2024-11-23 12:50:30.000000 UTC | Section
3000 |  | 11 KV | MODERATE | ANISH STUDIO | 41053 | KANDIVLI INDUSTRIES NO.1 | 2214 | 225+300 | PILC+XLPE | 2024-11-23 12:45:00.000000 UTC | 2024-11-23 12:45 | 11 | 2 | 44 | 2024-11-25 23:51:27.000000 UTC | 25 | 15 | 0 | 0 | EXCAVATION ALONG THE ROUTE | 1 | 1 | R phase faulty at a distance of 25 meters from Kandivli Industries No.1 Substation Switch Number 2214 . Fault pinpointed OPPSITE TO K.I.E NO 1 S/S . Shown to LINGAYA . Total length 302 meter. |  |  | 4 | Fault Bypassed |  | Fault Details |  | WINTER | 40 | 22.5 | 22.5 | 0.56 |  |  | O |  |  | K.I.E. REC-STN | 2024-11-23 13:23:08.000000 UTC | Section